## Schlegel
Date Last Updated |  | 2023-01-12
School Name: |  | Schlegel Road Elementary School
Lab ELAP ID# |  | NY63556 |  |  |  | Method of Analysis: |  |  | Metals 200.9
Lab ID# | School Sample ID # | Collection Date | Sample Location | Sample Location Description | Outlet Description | Initial/ Post Remediation | Lead Result mcg/L (ppb) | Lab Report Reciept Date | Action Taken for Outlets Greater than 15 mcg/L
SCH-01-CR-BY-101-T | 50 | 2021-04-06 | 101 | Room 101 Sink | Faucet | Initial | 882 | 2021-06-15 | WO#149076 - Replaced parts. 7/19/21. 1 - 3/4" gate valve, 3 - 1/2" 90's, 1 - 1/2" x 3/4" reducer, 2 - 1/2" x 3/8" compressions
SCH-01-CR-BY-101-T | 12 | 2021-08-06 | 101 | Room 101 Sink | Faucet | Post Remediation | 5.84 | 2021-08-13
SCH-01-CR-BY-103-T | 52 | 2021-04-06 | 103 | Room 103 Sink | Faucet | Initial | 12.4 | 2021-06-15
SCH-01-CR-BY-104-T | 57 | 2021-04-06 | 104 | Room 104 Sink | Faucet | Initial | 5.44 | 2021-06-15
SCH-01-CR-BY-106-T | 58 | 2021-04-06 | 106 | Room 106 Sink | Faucet | Initial | <5.00 | 2021-06-15
SCH-01-CR-BY-201-T | 29 | 2021-04-06 | 201 | Room 201 Sink | Faucet | Initial | 7.29 | 2021-06-15
SCH-01-CR-BY-203-T | 27 | 2021-04-06 | 203 | Room 203 Sink | Faucet | Initial | 8.98 | 2021-06-15
SCH-01-CR-BY-204-T | 23 | 2021-04-06 | 204 | Room 204 Sink | Faucet | Initial | <5.00 | 2021-06-15
SCH-01-CR-BY-206-T | 22 | 2021-04-06 | 206 | Room 206 Sink | Faucet | Initial | 9.04 | 2021-06-15
SCH-01-CR-BY-301-T | 21 | 2021-04-06 | 301 | Room 301 Sink | Faucet | Initial | 7.37 | 2021-06-15
SCH-01-CR-BY-303-T | 20 | 2021-04-06 | 303 | Room 303 Sink | Faucet | Initial | 8.79 | 2021-06-15
SCH-01-CR-BY-304-T | 13 | 2021-04-06 | 304 | Room 304 Sink | Faucet | Initial | 27.3 | 2021-06-15 | WO#149070 - 7/12/2021, Flush and change aerator.
SCH-01-CR-BY-304-T | 5 | 2021-08-06 | 304 | Room 304 Sink | Faucet | Post Remediation | <5.00 | 2021-08-13
SCH-01-CR-BY-306-T | 9 | 2021-04-06 | 306 | Room 306 Sink | Faucet | Initial | <5.00 | 2021-06-15
SCH-01-CR-IN-402-T | 51 | 2021-04-06 | 402 | Room 402 Sink | Faucet | Initial | 11.9 | 2021-06-15
SCH-01-HA-BY-402-B | 17 | 2022-09-21 | 402 | Classroom 402 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
SCH-01-CR-BY-406-T | 56 | 2021-04-06 | 406 | Room 406 Sink | Faucet | Initial | 8.59 | 2021-06-15
SCH-01-CR-BY-408-T | 19 | 2021-04-06 | 408 | Room 408 Sink | Faucet | Initial | <5.00 | 2021-06-15
SCH-01-CR-IN-409-LT | 10 | 2021-04-06 | 409 | Art Room Left Sink As You Enter Room And Turn 90 Degrees To The Right | Faucet | Initial | 10.6 | 2021-06-15
SCH-01-CR-IN-409-RT | 11 | 2021-04-06 | 409 | Art Room Right Sink As You Enter Room And Turn 90 Degrees To The Left | Faucet | Initial | 19.9 | 2021-06-15 | WO#149068 - 7/12/2021. Replaced 2 faucets, 4 - 1/2" 90's, 2- 1/2"gate valves, 2 - 1/2" x 3/8" compressions, 2 - chrome supplies
SCH-01-CR-IN-409-LT | 2 | 2021-08-06 | 409 | Art Room Left Sink As You Enter Room And Turn 90 Degrees To The Right | Faucet | Post Remediation | 7.56 | 2021-06-15
SCH-01-CR-IN-409-RT | 3 | 2021-08-06 | 409 | Art Room Right Sink As You Enter Room And Turn 90 Degrees To The Left | Faucet | Post Remediation | 7.54 | 2021-08-13
SCH-01-CR-IN-410-T | 12 | 2021-04-06 | 410 | Art Room Back Room Sink | Faucet | Initial | 22.7 | 2021-06-15 | WO#149069 - 7/12/2021, Flush and change aerator.
SCH-01-CR-IN-410-T | 4 | 2021-08-06 | 410 | Art Room Back Room Sink | Faucet | Post Remediation | 6.54 | 2021-08-13
SCH-01-RM-IN-502-T | 28 | 2021-04-06 | 502 | Library Office Sink | Faucet | Initial | 161 | 2021-06-15 | WO#149072 - 7/12/2021, Flush and change aerator.
SCH-01-RM-IN-502-T | 7 | 2021-08-06 | 502 | Library Office Sink | Faucet | Post Remediation | 12.1 | 2021-08-13
SCHL-01-OF-IN-LIB-T | 1 | 2022-12-28 | 502 | Library Office Sink | Faucet | Initial | 9 | 2023-01-05 | Area renovated, new fixture. Sampled 12/28/22
SCH-01-CR-IN-701-T | 49 | 2021-04-06 | 701 | Room 701 Sink | Faucet | Initial | <5.00 | 2021-06-15
SCH-01-RM-IN-701-B | 11 | 2021-08-06 | 701 | Room 701 Bottle Filler | Bottle Filler | Initial | 6.08 | 2021-08-13
SCH-01-CR-BY-702-T | 31 | 2021-04-06 | 702 | Room 702 Sink | Faucet | Initial | <5.00 | 2021-06-15
SCH-01-CR-BY-702-B | 5 | 2022-02-23 | 702 | Room 702 Bubbler | Bubbler | Initial | <5.00 | 2022-03-08
SCH-01-CR-IN-702-B | 1 | 2022-09-21 | 702 | Classroom 702 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
SCH-01-CR-IN-706-T | 7 | 2021-04-06 | 706 | Room 706 Sink | Faucet | Initial | <5.00 | 2021-06-15
SCH-01-CR-IN-706-B | 3 | 2022-02-23 | 706 | Room 706 Bubbler | Bubbler | Initial | <5.00 | 2022-03-08
SCH-01-CR-IN-707-T | 8 | 2021-04-06 | 707 | Room 707 Sink | Faucet | Initial | <5.00 | 2021-06-15
SCH-01-CR-IN-707-B | 4 | 2022-02-23 | 707 | Room 707 Bubbler | Bubbler | Initial | <5.00 | 2022-03-08
SCH-01-CR-IN-708-T | 6 | 2021-04-06 | 708 | Room 708 Sink | Faucet | Initial | <5.00 | 2021-06-15
SCH-01-CR-IN-708-B | 2 | 2022-02-23 | 708 | Room 708 Bubbler | Bubbler | Initial | <5.00 | 2022-03-08
SCH-01-CR-IN-709-T | 5 | 2021-04-06 | 709 | Room 709 Sink | Faucet | Initial | <5.00 | 2021-06-15
SCH-01-CR-IN-709-BF | 1 | 2022-02-23 | 709 | Room 709 Bottle Filler | Bottle Filler | Initial | 5.8 | 2022-03-08
SCH-01-NO-IN-803-PS | 47 | 2021-04-06 | 803 | Porcelain Sink in Nurse's Office (Furthest From Hallway); PS = Porcelain Sink | Faucet | Initial | <5.00 | 2021-06-15
SCH-01-NO-IN-803-TS | 48 | 2021-04-06 | 803 | Nurses Office Stainless Steel Sink (TS = Stainless steel tap) | Faucet | Initial | 6.32 | 2021-06-15
SCH-01-RM-IN-805-T | 45 | 2021-04-06 | 805 | Faculty Breakroom Sink | Faucet | Initial | 6.76 | 2021-06-15
SCH-01-KI-IN-810-LT | 37 | 2021-04-06 | 810 | Left Side Kitchen Large Sink | Faucet | Initial | 5.29 | 2021-06-15
SCH-01-KI-IN-810-RT | 38 | 2021-04-06 | 810 | Right Side Kitchen Large Sink | Faucet | Initial | 11.1 | 2021-06-15
SCH-01-RM-IN-CF-CT | 40 | 2021-04-06 | 811 | Conference Room Coffee Tap | Coffee Tap | Initial | <5.00 | 2021-06-15
SCH-01-CAFÉ-IN-814-BF | 35 | 2021-04-06 | 814 | Cafeteria Drinking Water Filler | Bottle Filler | Initial | <5.00 | 2021-06-15
SCH-01-CAFÉ-IN-CAFÉ-DF | 6 | 2022-03-31 | 814 | Drinking Fountain in Cafeteria | Drinking Fountain | Initial | <5.00 | 2022-04-12
SCH-01-KI-IN-821-T | 39 | 2021-04-06 | 821 | Small Kitchen Wash Sink | Faucet | Initial | 24.8 | 2021-06-15 | WO#149074 - 7/12/2021, Flush and change aerator.
SCH-01-KI-IN-821-T | 9 | 2021-08-06 | 821 | Small Kitchen Wash Sink | Faucet | Post Remediation | 13.7 | 2021-08-13
SCH-01-RM-IN-T12-T | 30 | 2021-04-06 | 605 Restroom | Gym Western Office Sink | Faucet | Initial | 15.9 | 2021-06-15 | WO#149073 - 7/12/2021, Flush and change aerator.
SCH-01-RM-IN-T12-T | 8 | 2021-08-06 | 605 Restroom | Gym Western Office Sink | Faucet | Post Remediation | 10.2 | 2021-08-13
SCH-01-RM-IN-T16-T | 36 | 2021-04-06 | 606 Restroom | East Gym Office Sink | Faucet | Initial | 9.84 | 2021-06-15
SCH-01-NO-IN-T3-PS | 46 | 2021-04-06 | 803 Restroom | Porcelain Sink in Nurse's Office (Closest to Hallway); aka restroom sink | Faucet | Initial | 5.43 | 2021-06-15
SCH-01-RM-IN-807A-T | 42 | 2021-04-06 | 807A | Band Room Sink | Faucet | Initial | 58 | 2021-06-15 | WO#149075 - 7/12/2021. Replaced faucet, 3 - 1/2" 90's, 1 - 1/2"gate valves, 1 - 1/2" x 3/8" reducer, 1 - chrome supply
SCH-01-RM-IN-807A-T | 10 | 2021-08-06 | 807A | Band Room Sink | Faucet | Post Remediation | 43.9 | 2021-06-15
SCH-01-GYM-IN-EGYM-DF | 2 | 2022-09-21 | Gym East Entry | East Girl's Gym Drinking Fountain | Drinking Fountain | Initial | 8.44 | 2022-10-05
SCH-01-GYM-IN-WGYM-DF | 3 | 2022-09-21 | Gym West Entry | West Boy's Gym Drinking Fountain | Drinking Fountain | Initial | 6.07 | 2022-10-05
SCH-01-HA-BY-101-B | 18 | 2022-09-21 | Hall by 101 | Hallway by 101 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
SCH-01-HA-BY-103-B | 16 | 2022-09-21 | Hall by 103 | Hallway by 103 Bubbler | Bubbler | Initial | 16.4 | 2022-10-05
SCH-01-HA-BY-103-B-R | 1 | 2022-10-18 | Hall by 103 | Hallway by 103 Bubbler RETEST | Bubbler | Post Remediation | 11.6 | 2022-11-01
SCH-01-HA-BY-104-B | 14 | 2022-09-21 | Hall by 104 | Hallway by 104 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
SCH-01-HA-BY-106-B | 13 | 2022-09-21 | Hall by 106 | Hallway by 106 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
SCH-01-HA-BY-201-B | 12 | 2022-09-21 | Hall by 201 | Hallway by 201 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
SCH-01-HA-BY-203-B | 11 | 2022-09-21 | Hall by 203 | Hallway by 203 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
SCH-01-HA-BY-204-B | 10 | 2022-09-21 | Hall by 204 | Hallway by 204 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
SCH-01-HA-BY-206-B | 9 | 2022-09-21 | Hall by 206 | Hallway by 206 Bubbler | Bubbler | Initial | 5.37 | 2022-10-05
SCH-01-HA-BY-301-B | 8 | 2022-09-21 | Hall by 301 | Hallway by 301 Bubbler | Bubbler | Initial | 8.95 | 2022-10-05
SCH-01-HA-BY-303-B | 7 | 2022-09-21 | Hall by 303 | Hallway by 303 Bubbler | Bubbler | Initial | 7.27 | 2022-10-05
SCH-01-HA-BY-304-DF | 4 | 2022-03-31 | Hall by 304 | Drinking Fountain by Room 304 | Drinking Fountain | Initial | <5.00 | 2022-04-12
SCH-01-HA-BY-304-B | 5 | 2022-09-21 | Hall by 304 | Hallway by 304 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
SCH-01-HA-BY-306-B | 4 | 2022-09-21 | Hall by 306 | Hallway by 306 Bubbler | Bubbler | Initial | 5.89 | 2022-10-05
SCH-01-HA-BY-405-BF | 53 | 2021-04-06 | Hall by 405 | Southside Water Filler | Bottle Filler | Initial | <5.00 | 2021-06-15
SCH-01-HA-BY-405-DF | 2 | 2022-03-31 | Hall by 405 | Drinking Fountain by 405, Outside Bathrooms | Drinking Fountain | Initial | <5.00 | 2022-04-12
SCH-01-HA-BY-406-B | 15 | 2022-09-21 | Hall by 406 | Hallway by 406 Bubbler | Bubbler | Initial | 5.89 | 2022-10-05
SCH-01-HA-BY-408-B | 6 | 2022-09-21 | Hall by 408 | Hallway by 308 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
SCH-01-HA-BY-805-B | 6 | 2022-02-23 | Hall by 805 | Bubbler Near Faculty Breakroom | Bubbler | Initial | 25.6 | 2022-03-08 | Replaced with bottle/ glass filler
SCH-01-HA-BY-805-BF | 1 | 2022-03-31 | Hall by 805 | Bottle Filler by 805 | Bottle Filler | Initial | 96.4 | 2022-04-12 | Formerly bubbler near faculty breakroom
SCH-01-HA-BY-CAFÉ-DF | 5 | 2022-03-31 | Hall by Cafeteria | Drinking Fountain by Cafeteria | Drinking Fountain | Initial | <5.00 | 2022-04-12
SCH-01-HA-BY-814-BF | 32 | 2021-04-06 | Hall by Gym | Gym Water Filler (near bathrooms) | Bottle Filler | Initial | <5.00 | 2021-06-15
SCH-01-HA-BY-NO-B | 3 | 2022-05-20 | Hall by Nurse | Hall Nurse Bottle Filler | Bottle Filler | Initial | <5.00 | 2022-05-27
SCH-01-HA-BY-T9-BF | 16 | 2021-04-06 | Hall by T9 Restroom | North Side Water Filler | Bottle Filler | Initial | <5.00 | 2021-06-15
SCH-01-HA-BY-500-BF | 25 | 2021-04-06 | Hall Near Library | East Entrance Water Filler | Bottle Filler | Initial | 16.6 | 2021-06-15 | WO#149071 - 7/12/2021. Replaced filter.
SCH-01-HA-BY-500-BF | 6 | 2021-08-06 | Hall near Library | East Entrance Water Filler | Bottle Filler | Post Remediation | <5.00 | 2021-08-13
SCH-01-HA-BY-E16-DF | 3 | 2022-03-31 | Hall near T6/T7 Restrooms | Drinking Fountain by E16 | Drinking Fountain | Initial | <5.00 | 2022-04-12
SCH-01-GT-IN-T1-T | 43 | 2021-04-06 | T1 Restroom | Faculty Restroom Right Sink (Facing Faculty Restrooms) | Faucet | Initial | <5.00 | 2021-06-15
SCH-01-GT-IN-T10-T | 14 | 2021-04-06 | T10 Restroom | Faculty Restroom Right Sink (Facing Faculty Restrooms) | Faucet | Initial | <5.00 | 2021-06-15
SCH-01-BT-IN-T11-T | 15 | 2021-04-06 | T11 Restroom | Faculty Restroom Left Sink (Facing Faculty Restrooms) | Faucet | Initial | 6.31 | 2021-06-15
SCH-01-GT-IN-T14-T | 33 | 2021-04-06 | T14 Restroom | Gym Girls Restroom Sink | Faucet | Initial | <5.00 | 2021-06-15
SCH-01-BT-IN-T15-T | 34 | 2021-04-06 | T15 Restroom | Gym Boys Restroom Sink | Faucet | Initial | <5.00 | 2021-06-15
SCH-01-RM-IN-T18-T | 41 | 2021-04-06 | T19 Restroom | Receiving Area Sink | Faucet | Initial | <5.00 | 2021-06-15
SCH-01-BT-IN-T2-T | 44 | 2021-04-06 | T2 Restroom | Faculty Restroom Left Sink (Facing Faculty Restrooms) | Faucet | Initial | <5.00 | 2021-06-15
SCH-01-BT-BY-711-RT | 1 | 2021-04-06 | T21 Restroom | Boys Restroom Right Sink Near Room 711 | Faucet | Initial | <5.00 | 2021-06-15
SCH-01-BT-BY-711-LT | 3 | 2021-04-06 | T21 Restroom | Boys Restroom Left Sink Near Room 711 | Faucet | Initial | 28.6 | 2021-06-15 | WO#149067 - 7/12/2021, Flush and change aerator.
SCH-01-BT-BY-711-LT | 1 | 2021-08-06 | T21 Restroom | Boys Restroom Left Sink Near Room 711 | Faucet | Post Remediation | <5.00 | 2021-08-13
SCH-01-GT-BY-711-LT | 2 | 2021-04-06 | T22 Restroom | Girls Restroom Left Sink Near Room 711 | Faucet | Initial | <5.00 | 2021-06-15
SCH-01-GT-BY-711-RT | 4 | 2021-04-06 | T22 Restroom | Girls Restroom Right Sink Near Room 711 | Faucet | Initial | <5.00 | 2021-06-15
SCH-01-GT-IN-T4-T | 55 | 2021-04-06 | T4 Restroom | Girls Restroom Sink (Southside of Building) | Faucet | Initial | 5.13 | 2021-06-15
SCH-01-BT-IN-T5-T | 54 | 2021-04-06 | T5 Restroom | Boys Restroom Sink (Southside of Building) | Faucet | Initial | <5.00 | 2021-06-15
SCH-01-BT-IN-T6-T | 26 | 2021-04-06 | T6 Restroom | Boys Restroom Sink (Eastside of Building) | Faucet | Initial | <5.00 | 2021-06-15
SCH-01-GT-IN-T7-T | 24 | 2021-04-06 | T7 Restroom | Girls Restroom Sink (Eastside of Building) | Faucet | Initial | <5.00 | 2021-06-15
SCH-01-GT-IN-T8-T | 17 | 2021-04-06 | T8 Restroom | Girls Restroom Sink (Northside of Building) | Faucet | Initial | <5.00 | 2021-06-15
SCH-01-BT-IN-T9-T | 18 | 2021-04-06 | T9 Restroom | Boys Restroom Sink (Northside of Building) | Faucet | Initial | <5.00 | 2021-06-15

## Klem Rd South
Date Last Updated |  | 2023-01-12
School Name: |  | Klem Road South Elementary School
Lab ELAP ID# |  | NY63556 |  |  |  | Method of Analysis: |  |  | Metals 200.9
Lab ID# | School Sample ID # | Collection Date | Sample Location | Sample Location Description | Outlet Description | Initial/ Post Remediation | Lead Result mcg/L (ppb) | Lab Report Reciept Date | Action Taken for Outlets Greater than 15 mcg/L
KS-01-HA-BY-101-T | 51 | 2021-04-08 | 101 | Room 101 Sink Fixture | Faucet | Initial | 5.53 | 2021-06-15
KS-01-HA-BY-101-B | 19 | 2022-09-21 | 101 | Hallway by 101 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
KS-01-HA-BY-103-T | 53 | 2021-04-08 | 103 | Room 103 Sink Fixture | Faucet | Initial | 18.3 | 2021-06-15 | WO#149090 - 7/9/2021. Replaced 2 - 1/2" 90s, 1 - gate valve, 1 - ball valve, 1 - 1/2" T.
KS-01-HA-BY-103-T | 26 | 2021-08-06 | 103 | Room 103 Sink Fixture | Faucet | Post Remediation | 13.7 | 2021-08-13
KS-01-HA-BY-103-B | 17 | 2022-09-21 | 103 | Hallway by 103 Bubbler | Bubbler | Initial | 8.27 | 2022-10-05
KS-01-HA-BY-104-T | 58 | 2021-04-08 | 104 | Room 104 Sink Fixture | Faucet | Initial | 6.21 | 2021-06-15
KS-01-HA-BY-104-B | 15 | 2022-09-21 | 104 | Hallway by 104 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
KS-01-HA-BY-106-T | 30 | 2021-04-08 | 106 | Room 106 Sink Fixture | Faucet | Initial | 50.9 | 2021-06-15 | WO#149082 - 7/10/2021. Replaced fittings. 2 - 1/2" 90s, 2 - 1/2" gate valves, 2 - 1/2" x 3/8" compression fittings.
KS-01-HA-BY-106-T | 18 | 2021-08-06 | 106 | Room 106 Sink Fixture | Faucet | Post Remediation | <5.00 | 2021-08-13
KS-01-HA-BY-106-B | 14 | 2022-09-21 | 106 | Hallway by 106 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
KS-01-HA-BY-201-T | 29 | 2021-04-08 | 201 | Room 201 Sink Fixture | Faucet | Initial | 38.2 | 2021-06-15 | WO#149081 - 7/10/2021. Replaced fittings. 1 - gate vlave, 4 - 1/2" 90s, 1 - 1/2" 45, 1 - 1/2" T, 2 - 1/2" x 3/8" compression fittings, 1 - ball valve.
KS-01-HA-BY-201-T | 17 | 2021-08-06 | 201 | Room 201 Sink Fixture | Faucet | Post Remediation | 6.34 | 2021-08-13
KS-01-HA-BY-201-B | 13 | 2022-09-21 | 201 | Hallway by 201 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
KS-01-HA-BY-203-T | 27 | 2021-04-08 | 203 | Room 203 Sink Fixture | Faucet | Initial | 25.4 | 2021-06-15 | WO#149079 - 7/9/2021. Replaced fittings. 1 - 1/2" brass 90. 1 - 1/2" chrome stop. 1 - 1/2" T, 1 - 3/8" x 1/2" compression, 1 - ball valve.
KS-01-HA-BY-203-T | 14 | 2021-08-06 | 203 | Room 203 Sink Fixture | Faucet | Post Remediation | <5.00 | 2021-08-13
KS-01-HA-BY-203-B | 12 | 2022-09-21 | 203 | Hallway by 203 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
KS-01-HA-BY-204-T | 23 | 2021-04-08 | 204 | Room 204 Sink Fixture | Faucet | Initial | <5.00 | 2021-06-15
KS-01-HA-BY-204-B | 11 | 2022-09-21 | 204 | Hallway by 204 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
KS-01-HA-BY-206-T | 22 | 2021-04-08 | 206 | Room 206 Sink Fixture | Faucet | Initial | 20.6 | 2021-06-15 | WO#149078 - 7/23/2021. Flush and replace aerator.
KS-01-HA-BY-206-T | 14 | 2021-08-06 | 206 | Room 206 Sink Fixture | Faucet | Post Remediation | 6.53 | 8.13/2021
KS-01-HA-BY-206-B | 10 | 2022-09-21 | 206 | Hallway by 206 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
KS-01-HA-BY-301-T | 20 | 2021-04-08 | 301 | Room 301 Sink Fixture | Faucet | Initial | 9.79 | 2021-06-15
KS-01-HA-BY-301-B | 9 | 2022-09-21 | 301 | Hallway by 301 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
KS-01-HA-BY-303-T | 19 | 2021-04-08 | 303 | Room 303 Sink Fixture | Faucet | Initial | 6.71 | 2021-06-15
KS-01-HA-BY-303-B | 8 | 2022-09-21 | 303 | Hallway by 303 Bubbler | Bubbler | Initial | 6.42 | 2022-10-05
KS-01-HA-BY-304-T | 12 | 2021-04-08 | 304 | Room 304 Sink Fixture | Faucet | Initial | 7.67 | 2021-06-15
KS-01-HA-BY-304-B | 6 | 2022-09-21 | 304 | Hallway by 304 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
KS-01-HA-BY-306-T | 9 | 2021-04-08 | 306 | Room 306 Sink Fixture | Faucet | Initial | 23.7 | 2021-06-15 | WO#149077 - 7/9/2021. Replaced 2-ball valves, 4 - propress 90s, 2 - 1/2" x 3/8" adatpters, 2 - 12" braided supply lines.
KS-01-HA-BY-306-T | 13 | 2021-08-06 | 306 | Room 306 Sink Fixture | Faucet | Post Remediation | 7.1 | 2021-08-13
KS-01-HA-BY-306-B | 5 | 2022-09-21 | 306 | Hallway by 306 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
KS-01-CR-IN-402-T | 52 | 2021-04-08 | 402 | Room 402 Sink Fixture | Faucet | Initial | 20 | 2021-06-15 | WO#149089 - 7/22/2021. Flush,Replace aerator.
KS-01-CR-IN-402-T | 25 | 2021-08-06 | 402 | Room 402 Sink Fixture | Faucet | Post Remediation | 6.14 | 2021-08-13
KS-01-CR-IN-402-B | 18 | 2022-09-21 | 402 | Classroom 402 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
KS-01-HA-BY-405-T | 57 | 2021-04-08 | 405 | Room 405 Sink Fixture | Faucet | Initial | 15.5 | 2021-06-15 | WO#149091 - 7/22/2021. Flush and replace aerator.
KS-01-HA-BY-405-T | 27 | 2021-08-06 | 405 | Room 405 Sink Fixture | Faucet | Post Remediation | 5.04 | 2021-08-13
KS-01-HA-BY-405-B | 16 | 2022-09-21 | 405 | Hallway by 405 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
KS-01-HA-BY-407-T | 18 | 2021-04-08 | 407 | Room 407 Sink Fixture | Faucet | Initial | 12.1 | 2021-06-15
KS-01-HA-BY-407-B | 7 | 2022-09-21 | 407 | Hallway by 407 Bubbler | Bubbler | Initial | 5.8 | 2022-10-05
KS-01-HA-BY-502-T | 28 | 2021-04-08 | 502 | Room 502 Sink Fixture | Faucet | Initial | 19.9 | 2021-06-15 | WO#149080 - 7/9/2021. Removed 2 old gate valves. Installed 2 propress 1/2" ball valves.
KS-01-HA-BY-502-T | 16 | 2021-08-06 | 502 | Room 502 Sink Fixture | Faucet | Post Remediation | 12 | 2021-08-13
KS-01-CR-IN-502-T | 2 | 2022-12-28 | 502 | Classroom 502 Tap | Faucet | Initial | 11 | 2023-01-05 | Sampled 12/28/22
KS-01-CR-IN-503-T | 21 | 2021-04-08 | 503 | Room 503 Sink Fixture | Faucet | Initial | 9.01 | 2021-06-15
KS-01-OF-IN-503-T | 1 | 2022-12-28 | 503 | 503 Office Tap | Faucet | Initial | 5 | 2023-01-05 | Sampled 12/28/22
KS-01-GY-IN-605-T | 38 | 2021-04-08 | 605 | Eastern Gym Office Sink | Faucet | Initial | 31.6 | 2021-06-15 | WO#149085 - 7/23/2021. Flush and replace aerator.
KS-01-OF-IN-503-T | 21 | 2021-08-06 | 605 | Eastern Gym Office Sink | Faucet | Post Remediation | 30.3 | 2021-08-13
KS-01-OFF-IN-CO-T | 4 | 2022-09-21 | 605 | Eastern Gym Office Sink (Gym Coach's Office Tap) | Faucet | Post Remediation | 10.1 | 2022-10-05
KS-01-GY-IN-606-T | 31 | 2021-04-08 | 606 | Western Gym Office Sink | Faucet | Initial | 23.5 | 2021-06-15 | WO#149083 - 7/23/2021. Flush and replace aerator.
KS-01-GY-IN-606-T | 19 | 2021-08-06 | 606 | Western Gym Office Sink | Faucet | Post Remediation | 14.4 | 2021-08-13
KS-01-CR-IN-701-T | 50 | 2021-04-08 | 701 | Room 701 Sink Fixture | Faucet | Initial | 8.37 | 2021-06-15
KS-01-CR-IN-701-B | 6 | 2022-02-23 | 701 | Room 701 Bubbler | Bubbler | Initial | 6.63 | 2022-03-08
KS-01-CR-IN-702-T | 33 | 2021-04-08 | 702 | Room 702 Sink Fixture | Faucet | Initial | 7.54 | 2021-06-15
KS-01-CR-IN-702-DF | 5 | 2022-02-23 | 702 | Room 702 Drinking Fountain | Drinking Fountain | Initial | 18.4 | 2022-03-08
KS-01-CR-IN-702-DF | 1 | 2022-03-31 | 702 | Room 702 Drinking Fountain | Drinking Fountain | Post Remediation | 15.9 | 2022-04-12
KS-01-CR-IN-702B | 1 | 2022-09-21 | 702 | Room 702 Drinking Fountain | Bubbler | Post Remediation | 5.32 | 2022-10-05
KS-01-CR-IN-706-T | 5 | 2021-04-08 | 706 | Room 706 Sink Fixture | Faucet | Initial | 6.41 | 2021-06-15
KS-01-CR-IN-706-BF | 1 | 2022-02-23 | 706 | Room 706 Bottle Filler | Bottle Filler | Initial | 11.8 | 2022-03-08
KS-01-CR-IN-707-T | 6 | 2021-04-08 | 707 | Room 707 Sink Fixture | Faucet | Initial | 8.69 | 2021-06-15
KS-01-CR-IN-707-BF | 2 | 2022-02-23 | 707 | Room 707 Bottle Filler | Bottle Filler | Initial | <5.00 | 2022-03-08
KS-01-CR-IN-708-T | 8 | 2021-04-08 | 708 | Room 708 Sink Fixture | Faucet | Initial | 6.49 | 2021-06-15
KS-01-CR-IN-708-BF | 4 | 2022-02-23 | 708 | Room 708 Bottle Filler | Bottle Filler | Initial | 20 | 2022-03-08
KS-01-CR-IN-708-BF | 4 | 2022-03-31 | 708 | Room 708 Bottle Filler | Bottle Filler | Post Remediation | <5.00 | 2022-04-12
KS-01-CR-IN-709-T | 7 | 2021-04-08 | 709 | Room 709 Sink Fixture | Faucet | Initial | 7.11 | 2021-06-15
KS-01-CR-IN-709-BF | 3 | 2022-02-23 | 709 | Room 709 Bottle Filler | Bottle Filler | Initial | <5.00 | 2022-03-08
KS-01-NO-IN-803-T2 | 48 | 2021-04-08 | 803 | Porcelain Sink in Nurse's Office (Closest to Hallway) | Faucet | Initial | 15.2 | 2021-06-15 | WO#149088 - 7/22/2021. Flush and replace aerator.
KS-01-NO-IN-803-T1 | 49 | 2021-04-08 | 803 | Porcelain Sink in Nurse's Office (Furthest From Hallway) | Faucet | Initial | <5.00 | 2021-06-15
KS-01-NO-IN-803-T2 | 24 | 2021-08-06 | 803 | Porcelain Sink in Nurse's Office (Closest to Hallway) | Faucet | Post Remediation | 12.6 | 2021-08-13
KS-01-LUR-IN-805-T | 47 | 2021-04-08 | 805 | Sink Inside Faculty Lounge | Faucet | Initial | <5.00 | 2021-06-15
KS-01-CAFÉ-IN-810-T1 | 40 | 2021-04-08 | 810 | Left Handed Prep Sink (As You Face Sinks) in Kitchen | Faucet | Initial | <5.00 | 2021-06-15
KS-01-CAFÉ-IN-810-T2 | 41 | 2021-04-08 | 810 | Right Handed Prep Sink (As You Face Sinks) in Kitchen | Faucet | Initial | 12.9 | 2021-06-15
KS-01-CAFÉ-IN-810-T3 | 42 | 2021-04-08 | 810 | Small Hand Washing Station in Kitchen | Faucet | Initial | 8.37 | 2021-06-15
KS-01-BT-BY-812-T | 43 | 2021-04-08 | 812 | Receiving Area Restroom Sink | Faucet | Initial | <5.00 | 2021-06-15
KS-01-CAFÉ-IN-814-BF | 37 | 2021-04-08 | 814 | Water Filler in Cafeteria | Bottle Filler | Initial | <5.00 | 2021-06-15
KS-01-CR-IN-408-T1 | 10 | 2021-04-08 | 408 Art | Art Room Left Handed Sink As You Enter The Room And Turn 90 Degrees To The Left | Faucet | Initial | <5.00 | 2021-06-15
KS-01-CR-IN-408-T2 | 11 | 2021-04-08 | 408 Art | Art Room Right Handed Sink As You Enter The Room And Turn 90 Degrees To The Left | Faucet | Initial | 6.97 | 2021-06-15
KS-01-CR-IN-807A-T | 44 | 2021-04-08 | 807A | Band Room Sink | Faucet | Initial | 57.4 | 2021-06-15 | WO#149087 - 7/9/2021. Replaced 1 - 1/2" ball valve, 1 - 1/2" propress 90.
KS-01-CR-IN-807A-T | 23 | 2021-08-06 | 807A | Band Room Sink | Faucet | Post Remediation | 12 | 2021-08-13
KS-01-CR-IN-807-T | 20 | 2022-09-21 | 807A | Music Storage Room Sink | Faucet | Post Remediation | 13.7 | 2022-10-05
KS-01-GYM-IN-EGYM-DF | 3 | 2022-09-21 | East Gym Entry | East Boys Gym Drinking Fountain | Drinking Fountain | Initial | <5.00 | 2022-10-05
KS-01-HA-BY-T4-BF | 54 | 2021-04-08 | Hall Between T4 and T5 | Northside Water Filler (Between Boys and Girls Room) | Bottle Filler | Initial | <5.00 | 2021-06-15
KS-01-HA-BY-T9-BF | 15 | 2021-04-08 | Hall Between T8 and T9 | Southside Water Filler (Between Boys and Girls Room) | Bottle Filler | Initial | <5.00 | 2021-06-15
KS-01-HA-BY-304-DF | 5 | 2022-03-31 | Hall between T8 and T9 | Drinking Fountain by 304, Outside Bathrooms | Drinking Fountain | Initial | <5.00 | 2022-04-12
KS-01-HA-BY-404-DF | 7 | 2022-03-31 | Hall by 404 | Drinking Fountain by Room 404 | Drinking Fountain | Initial | <5.00 | 2022-04-12
KS-01-HA-BY-E16-DF | 6 | 2022-03-31 | Hall by Exit 16 | Drinking Fountain by Exit 16 | Drinking Fountain | Initial | <5.00 | 2022-04-12
KS-01-HA-BY-V2-BF | 25 | 2021-04-08 | Hall Near Vestibule V2 | West Entrance Water Filler | Bottle Filler | Initial | <5.00 | 2021-06-15
KS-01-HA-BY-805-B | 7 | 2022-02-23 | Hall Outside 805 | Bubbler Outside of Faculty Lounge | Bubbler | Initial | <5.00 | 2022-03-08
KS-01-HA-BY-CAFÉ-DF | 2 | 2022-03-31 | Hall outside Cafeteria | Drinking Fountain by Cafeteria | Drinking Fountain | Initial | <5.00 | 2022-04-12
KS-01-CAFÉ-IN-CAFÉ-DF | 3 | 2022-03-31 | Hall outside Cafeteria | Drinking Fountain in Cafeteria | Drinking Fountain | Initial | <5.00 | 2022-04-12
KS-01-BT-IN-T1-T | 45 | 2021-04-08 | T1 Restroom | Right Handed Sink of Restrooms Next to Faculty Lounge (As You Face the Restrooms) | Faucet | Initial | <5.00 | 2021-06-15
KS-01-GT-IN-T10-T | 13 | 2021-04-08 | T10 Restroom | Faculty Restroom Right Sink (As You Face Restroom Doors) | Faucet | Initial | <5.00 | 2021-06-15
KS-01-BT-IN-T11-T | 14 | 2021-04-08 | T11 Restroom | Faculty Restroom Left Sink (As You Face Restroom Doors) | Faucet | Initial | <5.00 | 2021-06-15
KS-01-GY-IN-T13-T | 32 | 2021-04-08 | T13 Restroom | Western Gym Locker Room Sink | Faucet | Initial | 20.9 | 2021-06-15 | WO#149084 - 7/23/2021. Flush and replace aerator.
KS-01-GY-IN-T13-T | 20 | 2021-08-06 | T13 Restroom | Western Gym Locker Room Sink | Faucet | Post Remediation | 15 | 2021-08-13
KS-01-HA-BY-T14-BF | 34 | 2021-04-08 | T14 Restroom | Gym Bathroom Water Filler | Bottle Filler | Initial | <5.00 | 2021-06-15
KS-01-GT-IN-T14-T | 35 | 2021-04-08 | T14 Restroom | Girls Restroom Near Gym Sink | Faucet | Initial | <5.00 | 2021-06-15
KS-01-BT-IN-T15-T | 36 | 2021-04-08 | T15 Restroom | Boys Restroom Near Gym Sink | Faucet | Initial | <5.00 | 2021-06-15
KS-01-LOR-IN-T17-T | 39 | 2021-04-08 | T17 Restroom | Eastern Gym Locker Room Sink | Faucet | Initial | 64.1 | 2021-06-15 | WO#149086 - 7/22/2021, Flush and change aerator.
KS-01-LOR-IN-T17-T | 22 | 2021-08-06 | T17 Restroom | Eastern Gym Locker Room Sink | Faucet | Post Remediation | 21.4 | 2021-08-13
KS-01-BT-IN-T19-T2 | 1 | 2021-04-08 | T19 Restroom | Boys Rest Room Near Room 705 Right Sink | Faucet | Initial | <5.00 | 2021-06-15
KS-01-BT-IN-T19-T1 | 3 | 2021-04-08 | T19 Restroom | Boys Rest Room Near Room 705 Left Sink | Faucet | Initial | <5.00 | 2021-06-15
KS-01-GT-IN-T2-T | 46 | 2021-04-08 | T2 Restroom | Left Handed Sink of Restrooms Next to Faculty Lounge (As You Face the Restrooms) | Faucet | Initial | <5.00 | 2021-06-15
KS-01-GT-IN-T20-T1 | 2 | 2021-04-08 | T20 Restroom | Girls Rest Room Near Room 705 Left Sink | Faucet | Initial | <5.00 | 2021-06-15
KS-01-GT-IN-T20-T2 | 4 | 2021-04-08 | T20 Restroom | Girls Rest Room Near Room 705 Right Sink | Faucet | Initial | <5.00 | 2021-06-15
KS-01-BT-IN-T4-T | 55 | 2021-04-08 | T4 Restroom | Boys Restroom Sink (North Side of Building) | Faucet | Initial | <5.00 | 2021-06-15
KS-01-GT-IN-T5-T | 56 | 2021-04-08 | T5 Restroom | Girls Restroom Sink (North Side of Building) | Faucet | Initial | <5.00 | 2021-06-15
KS-01-BT-IN-T6-T | 26 | 2021-04-08 | T6 Restroom | Boys Restroom Sink (West Side of Building) | Faucet | Initial | <5.00 | 2021-06-15
KS-01-GT-IN-T7-T | 24 | 2021-04-08 | T7 Restroom | Girls Restroom Sink (West Side of Building) | Faucet | Initial | <5.00 | 2021-06-15
KS-01-GT-IN-T8-T | 16 | 2021-04-08 | T8 Restroom | Girls Restroom Sink (South Side of Building) | Faucet | Initial | <5.00 | 2021-06-15
KS-01-BT-IN-T9-T | 17 | 2021-04-08 | T9 Restroom | Boys Restroom Sink (South Side of Building) | Faucet | Initial | <5.00 | 2021-06-15
KS-01-GYM-IN-WGYM-DF | 2 | 2022-09-21 | West Gym Entry | West Girls Gym Drinking Fountain | Drinking Fountain | Initial | 12.8 | 2022-10-05

## Plank Rd South
Date Last Updated |  | 2023-01-12
School Name: |  | Plank Road South Elementary School
Lab ELAP ID# |  | NY63556 |  |  |  | Method of Analysis: |  |  | Metals 200.9
Lab ID# | School Sample ID # | Collection Date | Sample Location | Sample Location Description | Outlet Description | Initial/ Post Remediation | Lead Result mcg/L (ppb) | Lab Report Reciept Date | Action Taken for Outlets Greater than 15 mcg/L
PS-01-HA-BY-001-T | 52 | 2021-04-13 | 1 | Room 1 Sink | Faucet | Initial | 13.4 | 2021-06-15
PS-01-HA-BY-1-B | 18 | 2022-09-22 | 1 | Hallway by 1 Bubbler | Bubbler | Initial | 9.19 | 2022-10-05
PS-01-HA-BY-003-T | 54 | 2021-04-13 | 3 | Room 3 Sink | Faucet | Initial | 8.21 | 2021-06-15
PS-01-HA-BY-3-B | 16 | 2022-09-22 | 3 | Hallway by 3 Bubbler | Bubbler | Initial | 7.39 | 2022-10-05
PS-01-HA-BY-004-T | 59 | 2021-04-13 | 4 | Room 4 Sink | Faucet | Initial | <5.00 | 2021-06-15
PS-01-HA-BY-4-B | 14 | 2022-09-22 | 4 | Hallway by 4 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
PS-01-HA-BY-006-T | 60 | 2021-04-13 | 6 | Room 6 Sink | Faucet | Initial | <5.00 | 2021-06-15
PS-01-HA-BY-6-B | 13 | 2022-09-22 | 6 | Hallway by 6 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
PS-01-HA-BY-007-T | 30 | 2021-04-13 | 7 | Room 7 Sink | Faucet | Initial | 10.2 | 2021-06-15
PS-01-HA-BY-7-B | 12 | 2022-09-22 | 7 | Hallway by 7 Bubbler | Bubbler | Initial | 6.69 | 2022-10-05
PS-01-HA-BY-009-T | 28 | 2021-04-13 | 9 | Room 9 Sink | Faucet | Initial | <5.00 | 2021-06-15
PS-01-HA-BY-9-B | 11 | 2022-09-22 | 9 | Hallway by 9 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
PS-01-HA-BY-010-T | 24 | 2021-04-13 | 10 | Room 10 Sink | Faucet | Initial | 5.82 | 2021-06-15
PS-01-HA-BY-10-B | 10 | 2022-09-22 | 10 | Hallway by 10 Bubbler | Bubbler | Initial | 5.26 | 2022-10-05
PS-01-HA-BY-013-T | 12 | 2021-04-13 | 13 | Room 13 Sink | Faucet | Initial | <5.00 | 2021-06-15
PS-01-HA-BY-13-B | 9 | 2022-09-22 | 13 | Hallway by 13 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
PS-01-HA-BY-015-T | 11 | 2021-04-13 | 15 | Room 15 Sink | Faucet | Initial | 7.3 | 2021-06-15
PS-01-HA-BY-15-B | 8 | 2022-09-22 | 15 | Hallway by 15 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
PS-01-HA-BY-016-T | 4 | 2021-04-13 | 16 | Room 16 Sink | Faucet | Initial | 9.2 | 2021-06-15
PS-01-HA-BY-16-B | 6 | 2022-09-22 | 16 | Hallway by 16 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
PS-01-HA-BY-018-T | 1 | 2021-04-13 | 18 | Room 18 Sink | Faucet | Initial | <5.00 | 2021-06-15
PS-01-HA-BY-18-B | 5 | 2022-09-22 | 18 | Hallway by 18 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
PS-01-HA-BY-019-T | 10 | 2021-04-13 | 19 | Room 19 Sink | Faucet | Initial | <5.00 | 2021-06-15
PS-01-HA-BY-19-B | 7 | 2022-09-22 | 19 | Hallway by 19 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
PS-01-HA-BY-021-T | 58 | 2021-04-13 | 21 | Room 21 Sink | Faucet | Initial | 102 | 2021-06-15 | WO#149102 - 7/3/2021. Replaced fittings. 1 - 1/2" ball valve, 1 - 1/2" T, 3 - 90s, 2 - 1/2" x 3/8" compression.
PS-01-HA-BY-021-T | 18 | 2021-08-11 | 21 | Room 21 Sink | Faucet | Post Remediation | <5.00 | 2021-08-23
PS-01-HA-BY-12-B | 15 | 2022-09-22 | 21 | Hallway by 21 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
PS-01-HA-BY-023-T | 53 | 2021-04-13 | 23 | Room 23 Sink | Faucet | Initial | 148 | 2021-06-15 | WO#149101 - 7/3/2021. Replaced fittings. 1 - 1/2" gate valve. 4 - 1/2" 90s, 1 - 1/2" T, 2 - 1/2" ball valves, 2 - 1/2" x 3/8" compression.
PS-01-CR-IN-23-B | 17 | 2022-09-22 | 23 | Classroom 23 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
PS-01-HA-BY-023-T | 17 | 8/11/212 | 23 | Room 23 Sink | Faucet | Post Remediation | <5.00 | 2021-08-23
PS-01-CR-IN-024-T1 | 2 | 2021-04-13 | 24 | Art Room Sink (Closest to Door) | Faucet | Initial | 6.49 | 2021-06-15
PS-01-CR-IN-024-T2 | 3 | 2021-04-13 | 24 | Art Room Sink (Furthest From Door) | Faucet | Initial | 8.9 | 2021-06-15
PS-01-CR-IN-024-T | 51 | 2021-04-13 | 24 | Room 24 Sink | Faucet | Initial | 15.4 | 2021-06-15 | WO#149100 - 8/2/2021. Replaced fittings. 1 - 1/2" ball valve, 2 - 1/2" 90s, 1 - 3/8" brass T.
PS-01-CR-IN-024-T | 15 | 2021-08-11 | 24 | Room 24 Sink | Faucet | Post Remediation | <5.00 | 2021-08-23
PS-01-CR-IN-024-BF | 16 | 2021-08-11 | 24 | Room 24 Bottle Filler | Bottle Filler | Initial | <5.00 | 2021-08-23
PS-01-CR-IN-026-T | 33 | 2021-04-13 | 26 | Room 26 Sink | Faucet | Initial | <5.00 | 2021-06-15
PS-01-CR-IN-026-B | 6 | 2022-02-24 | 26 | Room 26 Drinking Fountain | Drinking Fountain | Initial | <5.00 | 2022-03-08
PS-01-CR-IN-26-BF | 1 | 2022-09-22 | 26 | Classroom 26 Bottle Filler | Bottle Filler | Initial | <5.00 | 2022-10-05
PS-01-NO-IN-031-T1 | 48 | 2021-04-13 | 31 | Nurse's Office Porcelain Sink (Closest to Hallway) | Faucet | Initial | 6.58 | 2021-06-15
PS-01-NO-IN-031-T2 | 49 | 2021-04-13 | 31 | Nurse's Office Porcelain Sink (Furthest from Hallway) | Faucet | Initial | 6.09 | 2021-06-15
PS-01-LUR-IN-032-T | 47 | 2021-04-13 | 32 | Faculty Lounge Sink | Faucet | Initial | 10.4 | 2021-06-15
PS-01-LUR-IN-032-T | 47 | 2021-04-13 | 32 | Faculty Lounge Sink | Faucet | Initial | 10.4 | 2021-06-15
PS-01-CAFÉ-IN-036-BF | 37 | 2021-04-13 | 36 | Cafeteria Water Filler | Bottle Filler | Initial | <5.00 | 2021-06-15
PS-01-OF-IN-35 | 1 | 2022-03-31 | 35 | 35 Office Tap | Faucet | Initial | 11 | 2023-01-05 | Sampled 12/28/22
PS-01-CR-IN-602-T | 19 | 2021-04-13 | 602 | Room 602 Sink | Faucet | Initial | <5.00 | 2021-06-15
PS-01-CR-IN-602-BF | 1 | 2022-02-24 | 602 | Room 602 Bottle Filler | Bottle Filler | Initial | 6.59 | 2022-03-08
PS-01-CR-IN-603-T | 20 | 2021-04-13 | 603 | Room 603 Sink | Faucet | Initial | 6.34 | 2021-06-15
PS-01-CR-IN-603-BF | 2 | 2022-02-24 | 603 | Room 603 Bottle Filler | Bottle Filler | Initial | <5.00 | 2022-03-08
PS-01-CR-IN-607-T | 23 | 2021-04-13 | 607 | Room 607 Sink | Faucet | Initial | 10.6 | 2021-06-15
PS-01-CR-IN-607-BF | 5 | 2022-02-24 | 607 | Room 607 Bottle Filler | Bottle Filler | Initial | 7.19 | 2022-03-08
PS-01-CR-IN-608-T | 22 | 2021-04-13 | 608 | Room 608 Sink | Faucet | Initial | 14.9 | 2021-06-15
PS-01-CR-IN-608-BF | 4 | 2022-02-24 | 608 | Room 608 Bottle Filler | Bottle Filler | Initial | 24.3 | 2022-03-08
PS-01-CR-IN-608-BF | 5 | 2022-03-31 | 608 | Room 608 Bottle Filler | Drinking Fountain | Initial | <5.00 | 2022-04-12
PS-01-CR-IN-609-T | 21 | 2021-04-13 | 609 | Room 609 Sink | Faucet | Initial | <5.00 | 2021-06-15
PS-01-CR-IN-609-BF | 3 | 2022-02-24 | 609 | Room 609 Bottle Filler | Bottle Filler | Initial | 39.1 | 2022-03-08
PS-01-CR-IN-609-BF | 4 | 2022-03-31 | 609 | Room 609 Bottle Filler | Drinking Fountain | Initial | <5.00 | 2022-04-12
PS-01-HA-BY-29-DF | 7 | 2022-03-31 | ? | Drinking Fountain by Classroom 29 (no classroom 29) | Drinking Fountain | Initial | <5.00 | 2022-04-12
PS-01-CR-IN-032-T | 44 | 2021-04-13 | 34A | Music Room Sink | Faucet | Initial | 57.3 | 2021-06-15 | WO#149099 - 8/2/2021. Replaced fittings. 4 - 90s, 1 - 1/2" gate valve, 1 - 1/2" x 3/8" compression.
PS-01-CR-IN-032-T | 14 | 2021-08-11 | 34A | Music Room Sink | Faucet | Post Remediation | 12.4 | 2021-08-23
PS-01-CR-IN-MUS-T | 20 | 2022-09-22 | 34A | Music Storage Room Tap | Faucet | Post Remediation | <5.00 | 2022-10-05
PS-01-BT-IN-035C-T | 43 | 2021-04-13 | 35C | Bathroom Sink - Receiving Area | Faucet | Initial | 10.9 | 2021-06-15
PS-01-CAFÉ-IN-036B-T1 | 40 | 2021-04-13 | 36B | Left Side Kitchen Wash Sink | Faucet | Initial | <5.00 | 2021-06-15
PS-01-CAFÉ-IN-036B-T3 | 42 | 2021-04-13 | 36B | Small Kitchen Wash Sink | Faucet | Initial | 13.3 | 2021-06-15
PS-01-CAFÉ-IN-036B-T2 | 41 | 2021-04-15 | 36B | Right Side Kitchen Wash Sink | Faucet | Initial | 21.1 | 2021-06-15 | WO#149098 - 8/2/2021. Replaced fittings. 1 - new faucet. 2 - 1/2" female 90s, 1 - 3" x 1/2" brass nipple, 1 - 1/2" ball valve.
PS-01-CAFÉ-IN-036B-T2 | 13 | 2021-08-11 | 36B | Right Side Kitchen Wash Sink | Faucet | Post Remediation | <5.00 | 2021-08-23
PS-01-GYM-IN-EGYM-DF | 3 | 2022-09-22 | 37 East Entry | East Boy's Gym Drinking Fountain | Drinking Fountain | Initial | 7.35 | 2022-10-05
PS-01-GYM-IN-WGYM-DF | 2 | 2022-09-22 | 37 West Entry | West Girl's Gym Drinking Fountain | Drinking Fountain | Initial | 14.5 | 2022-10-05
PS-01-GY-IN-038B-T | 38 | 2021-04-13 | 38B | East Gym Office Sink | Faucet | Initial | 27 | 2021-06-15 | WO#149096 - 7/29/2021. Flush and install new aerator.
PS-01-GY-IN-038B-T | 11 | 2021-08-11 | 38B | East Gym Office Sink | Faucet | Post Remediation | 19.4 | 2021-08-23
PS-01-OFF-IN-CO-T | 4 | 2022-09-22 | 38B | Gym Coach's Office Tap | Faucet | Post Remediation | 6.04 | 2022-10-05
PS-01-LOR-IN-038D-T | 39 | 2021-04-13 | 38D | East Gym Locker Room Sink | Faucet | Initial | 42.8 | 2021-06-15 | WO#149097 - 7/29/2021. Flush and install new aerator.
PS-01-LOR-IN-038D-T | 12 | 2021-08-11 | 38D | East Gym Locker Room Sink | Faucet | Post Remediation | 31.5 | 2021-08-23
PS-01-LOR-IN-039A-T | 32 | 2021-04-13 | 39A | West Gym Locker Room Sink | Faucet | Initial | 23.7 | 2021-06-15 | WO#149095 - 7/29/2021. Flush and install new aerator.
PS-01-LOR-IN-039A-T | 10 | 2021-08-11 | 39A | West Gym Locker Room Sink | Faucet | Post Remediation | 9.63 | 2021-08-23
PS-01-GY-IN-039C-T | 31 | 2021-04-13 | 39C | West Gym Office Sink | Faucet | Initial | 15.2 | 2021-06-15 | WO#149094 - 7/29/2021. Flush and install new aerator.
PS-01-GY-IN-039C-T | 9 | 2021-08-11 | 39C | West Gym Office Sink | Faucet | Post Remediation | 13.9 | 2021-08-23
PS-01-RM-IN-070C-T | 29 | 2021-04-13 | 70C | Library Office Sink | Faucet | Initial | 14.6 | 2021-06-15
PS-01-HA-BY-T12-BF | 55 | 2021-04-13 | Hall between T11 and T12 | Northern Water Filler | Bottle Filler | Initial | <5.00 | 2021-06-15
PS-01-HA-BY-T4-BF | 34 | 2021-04-15 | Hall between T3 and T4 | Gym Bathroom Water Filler | Bottle Filler | Initial | <5.00 | 2021-06-15
PS-01-HA-BY-16-DF | 3 | 2022-03-31 | Hall between T5 and T6 | Drinking Fountain by Classroom 16, Outside Bathrooms | Drinking Fountain | Initial | <5.00 | 2022-04-12
PS-01-HA-BY-T7-BF | 7 | 2021-04-13 | Hall between T7 and T8 | Southern Water Filler | Bottle Filler | Initial | <5.00 | 2021-06-15
PS-01-HA-BY-BR-BF | 19 | 2022-09-22 | Hall by 32 | Hallway by Break Room Bottle Filler | Bottle Filler | Initial | 15.2 | 2022-10-05
PS-01-HA-BY-BR-BF-R | 1 | 2022-10-18 | Hall by 32 | Hallway by Break Room Bottle Filler RETEST | Bottle Filler | Post Remediation | <5.00 | 2022-11-01
PS-01-HA-BY-CAFÉ-DF | 2 | 2022-03-31 | Hall by 36 | Drinking Fountain by Cafeteria | Drinking Fountain | Initial | <5.00 | 2022-04-12
PS-01-HA-BY-E15-DF | 6 | 2022-03-31 | Hall by Exit 15 | Drinking Fountain by Exit 15 | Drinking Fountain | Initial | <5.00 | 2022-04-12
PS-01-HA-BY-V7-BF | 26 | 2021-04-13 | Hall by Vestibule V7 | Western Entrance Water Filler | Bottle Filler | Initial | <5.00 | 2021-06-15
PS-01-BT-IN-T1-T | 45 | 2021-04-13 | T1 Restroom | Faculty Lounge Bathroom Right Sink (Facing Bathroom Doors) | Faucet | Initial | <5.00 | 2021-06-15
PS-01-BT-IN-T10-T | 27 | 2021-04-13 | T10 Restroom | Western Boys Restroom Sink | Faucet | Initial | <5.00 | 2021-06-15
PS-01-GT-IN-T11-T | 57 | 2021-04-13 | T11 Restroom | Northern Girls Restroom Sink | Faucet | Initial | <5.00 | 2021-06-15
PS-01-BT-IN-T12-T | 56 | 2021-04-13 | T12 Restroom | Northern Boys Restroom Sink | Faucet | Initial | <5.00 | 2021-06-15
PS-01-NO-IN-T13-T | 50 | 2021-04-13 | T13 Restroom | Nurse's Office Stainless Steel Sink | Faucet | Initial | 8.97 | 2021-06-15
PS-01-BT-IN-T14-T3 | 13 | 2021-04-13 | T14 Restroom | Boys Restroom Right Sink | Faucet | Initial | <5.00 | 2021-06-15
PS-01-BT-IN-T14-T2 | 14 | 2021-04-13 | T14 Restroom | Boys Restroom Middle Sink | Faucet | Initial | <5.00 | 2021-06-15
PS-01-BT-IN-T14-T1 | 15 | 2021-04-13 | T14 Restroom | Boys Restroom Left Sink | Faucet | Initial | <5.00 | 2021-06-15
PS-01-GT-IN-T15-T1 | 16 | 2021-04-13 | T15 Restroom | Girls Restroom Left Sink | Faucet | Initial | <5.00 | 2021-06-15
PS-01-GT-IN-T15-T2 | 17 | 2021-04-13 | T15 Restroom | Girls Restroom Middle Sink | Faucet | Initial | <5.00 | 2021-06-15
PS-01-GT-IN-T15-T3 | 18 | 2021-04-13 | T15 Restroom | Girls Restroom Right Sink | Faucet | Initial | <5.00 | 2021-06-15
PS-01-BT-IN-T2-T | 46 | 2021-04-13 | T2 Restroom | Faculty Lounge Bathroom Left Sink (Facing Bathroom Doors) | Faucet | Initial | <5.00 | 2021-06-15
PS-01-BT-IN-T3-T | 36 | 2021-04-13 | T3 Restroom | Gym Boys Restroom Sink | Faucet | Initial | <5.00 | 2021-06-15
PS-01-GT-IN-T4-T | 35 | 2021-04-13 | T4 Restroom | Gym Girls Restroom Sink | Faucet | Initial | <5.00 | 2021-06-15
PS-01-GT-IN-T5-T | 8 | 2021-04-13 | T5 Restroom | Girls Bathroom Sink (Left Side When Facing Student Restrooms) - On South Side of Building | Faucet | Initial | <5.00 | 2021-06-15
PS-01-BT-IN-T6-T | 9 | 2021-04-13 | T6 Restroom | Boys Bathroom Sink (Right Side When Facing Student Restrooms) - On South Side of Building | Faucet | Initial | <5.00 | 2021-06-15
PS-01-BT-IN-T7-T | 5 | 2021-04-13 | T7 Restroom | Right Faculty Bathroom Sink (Right Side When Facing Faculty Restrooms) - Room T7 | Faucet | Initial | <5.00 | 2021-06-15
PS-01-GT-IN-T8-T | 6 | 2021-04-13 | T8 Restroom | Left Faculty Bathroom Sink (Left Side When Facing Faculty Restrooms) - Room T8 | Faucet | Initial | 18.8 | 2021-06-15 | WO#149093 - 7/29/2021. Flush and install new aerator.
PS-01-GT-IN-T8-T | 8 | 2021-08-11 | T8 Restroom | Left Faculty Bathroom Sink (Left Side When Facing Faculty Restrooms) - Room T8 | Faucet | Post Remediation | <5.00 | 2021-08-23
PS-01-GT-IN-T9-T | 25 | 2021-04-13 | T9 Restroom | Western Girls Restroom Sink | Faucet | Initial | <5.00 | 2021-06-15

## Klem Rd North
Date Last Updated |  | 2023-01-12
School Name: |  | Klem Road North Elementary School
Lab ELAP ID# |  | NY63556 |  |  |  | Method of Analysis: |  |  | Metals 200.9
Lab ID# | School Sample ID # | Collection Date | Sample Location | Sample Location Description | Outlet Description | Initial/ Post Remediation | Lead Result mcg/L (ppb) | Lab Report Reciept Date | Action Taken for Outlets Greater than 15 mcg/L
KN-00-CR-IN-ART-T | 1 | 2021-04-15 | 11 | Old Art Room Sink | Faucet | Initial | 11.4 | 2021-06-15
KN-00-RM-IN-KI-T1 | 8 | 2021-04-15 | 17 | Kitchen Sink 1 (Moving Clockwise) | Faucet | Initial | 6.44 | 2021-06-15
KN-00-RM-IN-KI-T2 | 9 | 2021-04-15 | 17 | Kitchen Sink 2 (Moving Clockwise) | Faucet | Initial | <5.00 | 2021-06-15
KN-00-RM-IN-KI-T3 | 10 | 2021-04-15 | 17 | Kitchen Sink 3 (Moving Clockwise) | Faucet | Initial | 5.87 | 2021-06-15
KN-00-RM-IN-KI-T4 | 11 | 2021-04-15 | 17 | Kitchen Sink 4 (Moving Clockwise) | Faucet | Initial | 6.52 | 2021-06-15
KN-00-RM-IN-CF-T2 | 13 | 2021-04-15 | 19 | Cafeteria Right Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-00-RM-IN-CF-T1 | 14 | 2021-04-15 | 19 | Cafeteria Left Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-00-RM-IN-CF-DF | 1 | 2022-02-23 | 19 | Cafeteria Drinking Fountain | Drinking Fountain | Initial | <5.00 | 2022-03-08
KN-00-RM-IN-CF-BF | 2 | 2022-02-23 | 19 | Cafeteria Bottle Filler | Bottle Filler | Initial | <5.00 | 2022-03-08
KN-01-CR-IN-103-T | 1 | 2022-05-20 | 103 | Classroom 103 Sink | Faucet | Initial | <5.00 | 2022-05-27
KN-01-CR-IN-103-DF | 2 | 2022-05-20 | 103 | Classroom 103 Fountain | Drinking Fountain | Initial | <5.00 | 2022-05-27
KN-01-CR-IN-103-B | 32 | 2022-10-12 | 103 | Classroom 103 Bubbler | Bubbler | Initial | 5.4 | 2022-11-01 | New From Renovation
KN-01-CR-IN-103-T | 33 | 2022-10-12 | 103 | Classroom 103 Sink | Faucet | Initial | <5.00 | 2022-11-01 | New From Renovation
KN-01-RM-IN-GLR-T | 46 | 2021-04-15 | 158 | Girls Locker Room Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-01-GT-IN-WLR-T | 45 | 2021-04-15 | 186 | Female Phys Ed Teacher's Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-02-RM-IN-TL-T | 16 | 2021-04-15 | 199 | 2nd Floor Teacher's Lounge Sink | Faucet | Initial | 25.3 | 2021-06-15 | WO#149103 - 7/19/2021. Replaced fittings. 1- 1/2" gate valve. 2 - 1/2" 90s. 1 - 1/2" x 3/8" compression.
KN-02-RM-IN-TL-T | 28 | 2021-08-06 | 199 | 2nd Floor Teacher's Lounge Sink | Faucet | Post Remediation | 32.7 | 2021-08-13
KN-02-RM-IN-TL-T | 16 | 2021-08-27 | 199 | 2nd Floor Teacher's Lounge Sink | Faucet | Post Remediation | <5.00 | 2021-09-03
KN-02-CR-IN-201-T | 15 | 2021-04-15 | 201 | Classroom 201 Sink | Faucet | Initial | 11.9 | 2021-06-15
KN-02-CR-IN-202-T | 26 | 2021-04-15 | 202 | Classroom 202 Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-02-CR-IN-202-B | 3 | 2022-10-12 | 202 | Classroom 202 Bubbler | Bubbler | Initial | <5.00 | 2022-11-01
KN-02-CR-IN-204-T | 28 | 2021-04-15 | 204 | Classroom 204 Sink | Faucet | Initial | 5.62 | 2021-06-15
KN-02-CR-IN-204-B | 4 | 2022-10-12 | 204 | Classroom 204 Bubbler | Bubbler | Initial | <5.00 | 2022-11-01
KN-02-CR-IN-205-T | 27 | 2021-04-15 | 205 | Classroom 205 Sink | Faucet | Initial | 19.2 | 2021-06-15 | WO#149106 - 7/19/2021. Replaced fittings. 1 - 1/2" 90. 1 - Brass T. 1 - chrome stop.
KN-02-CR-IN-205-T | 31 | 2021-08-06 | 205 | Classroom 205 Sink | Faucet | Post Remediation | 6.07 | 2021-08-13
KN-02-CR-IN-205-B | 5 | 2022-10-12 | 205 | Classroom 205 Bubbler | Bubbler | Initial | <5.00 | 2022-11-01
KN-02-CR-IN-206-T | 30 | 2021-04-15 | 206 | Classroom 206 Sink | Faucet | Initial | 7.47 | 2021-06-15
KN-02-CR-IN-206-B | 6 | 2022-10-12 | 206 | Classroom 206 Bubbler | Bubbler | Initial | 6.3 | 2022-11-01
KN-02-CR-IN-207-T | 29 | 2021-04-15 | 207 | Classroom 207 Sink | Faucet | Initial | 19.9 | 2021-06-15 | WO#149107 - 7/19/2021. Replaced fittings. 1 - 1/2" 90. 1 - Brass T. 1 - Chrome stop.
KN-02-CR-IN-207-T | 32 | 2021-08-06 | 207 | Classroom 207 Sink | Faucet | Post Remediation | 10.5 | 2021-08-13
KN-02-CR-IN-207-B | 7 | 2022-10-12 | 207 | Classroom 207 Bubbler | Bubbler | Initial | <5.00 | 2022-11-01
KN-02-CR-IN-208-T | 32 | 2021-04-15 | 208 | Classroom 208 Sink | Faucet | Initial | 12.3 | 2021-06-15
KN-02-CR-IN-208-B | 8 | 2022-10-12 | 208 | Classroom 208 Bubbler | Bubbler | Initial | <5.00 | 2022-11-01
KN-02-CR-IN-209-T | 31 | 2021-04-15 | 209 | Classroom 209 Sink | Faucet | Initial | 6.19 | 2021-06-15
KN-02-CR-IN-209-B | 9 | 2022-10-12 | 209 | Classroom 209 Bubbler | Bubbler | Initial | 8.45 | 2022-11-01
KN-01-CR-IN-101-BF | 36 | 2022-10-12 | 101/142 | Classroom 101 Bottle Filler | Bottle Filler | Initial | <5.00 | 2022-11-01
KN-01-BT-IN-101-T | 73 | 2021-04-15 | 101/142 | Classroom 101 Bathroom Sink | Faucet | Initial | 12.2 | 2021-06-15
KN-01-CR-IN-101-T | 74 | 2021-04-15 | 101/142 | Classroom 101 Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-01-CR-IN-101-B | 7 | 2022-02-23 | 101/142 | Classroom 101 Bubbler | Bubbler | Initial | 15.3 | 2022-03-08
KN-01-CR-IN-101-DF | 5 | 2022-03-31 | 101/142 | Drinking Fountain in Room 101 | Drinking Fountain | Post Remediation | 8.54 | 2022-04-12
KN-01-CR-IN-102-BF | 37 | 2022-10-12 | 102/131 | Classroom 102 Bottle Filler | Bottle Filler | Initial | 5.54 | 2022-11-01
KN-01-BT-IN-102-T | 71 | 2021-04-15 | 102/131 | Classroom 102 Bathroom Sink | Faucet | Initial | 6.09 | 2021-06-15
KN-01-CR-IN-102-T | 72 | 2021-04-15 | 102/131 | Classroom 102 Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-01-CR-IN-102-B | 6 | 2022-02-23 | 102/131 | Classroom 102 Bubbler | Bubbler | Initial | 11.5 | 2022-03-08
KN-01-CR-IN-104-B | 34 | 2022-10-12 | 104/133 | Classroom 104 Bubbler | Bubbler | Initial | <5.00 | 2022-11-01 | New From Renovation
KN-01-CR-IN-104-T | 35 | 2022-10-12 | 104/133 | Classroom 104 Sink | Faucet | Initial | 11.9 | 2022-11-01 | New From Renovation
KN-01-CR-IN-104-T | 69 | 2021-04-15 | 104/133 | Classroom 104 Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-01-CR-IN-105-B | 28 | 2022-10-12 | 105/138 | Classroom 105 Bubbler | Bubbler | Initial | <5.00 | 2022-11-01 | New From Renovation
KN-01-CR-IN-105-T | 29 | 2022-10-12 | 105/138 | Classroom 105 Sink | Faucet | Initial | <5.00 | 2022-11-01 | New From Renovation
KN-01-CR-IN-105-T | 67 | 2021-04-15 | 105/138 | Classroom 105 Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-01-CR-IN-106-B | 30 | 2022-10-12 | 106/134 | Classroom 106 Bubbler | Bubbler | Initial | <5.00 | 2022-11-01 | New From Renovation
KN-01-CR-IN-106-T | 31 | 2022-10-12 | 106/134 | Classroom 106 Sink | Faucet | Initial | <5.00 | 2022-11-01 | New From Renovation
KN-01-CR-IN-106-T | 68 | 2021-04-15 | 106/134 | Classroom 106 Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-01-CR-IN-107-B | 24 | 2022-10-12 | 107/139 | Classroom 107 Bubbler | Bubbler | Initial | 5.98 | 2022-11-01 | New From Renovation
KN-01-CR-IN-107-T | 25 | 2022-10-12 | 107/139 | Classroom 107 Sink | Faucet | Initial | <5.00 | 2022-11-01 | New From Renovation
KN-01-CR-IN-107-T | 65 | 2021-04-15 | 107/139 | Classroom 107 Sink | Faucet | Initial | 8.67 | 2021-06-15
KN-01-CR-IN-103-T | 70 | 2021-04-15 | 107/139 | Classroom 107 Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-01-CR-IN-108-B | 26 | 2022-10-12 | 108/135 | Classroom 108 Bubbler | Bubbler | Initial | <5.00 | 2022-11-01 | New From Renovation
KN-01-CR-IN-108-T | 27 | 2022-10-12 | 108/135 | Classroom 108 Sink | Faucet | Initial | <5.00 | 2022-11-01 | New From Renovation
KN-01-CR-IN-108-T | 66 | 2021-04-15 | 108/135 | Classroom 108 Sink | Faucet | Initial | 7.17 | 2021-06-15
KN-01-CR-IN-109-B | 22 | 2022-10-12 | 109/140 | Classroom 109 Bubbler | Bubbler | Initial | <5.00 | 2022-11-01 | New From Renovation
KN-01-CR-IN-109-T | 23 | 2022-10-12 | 109/140 | Classroom 109 Sink | Faucet | Initial | 13.4 | 2022-11-01 | New From Renovation
KN-01-CR-IN-109-T | 62 | 2021-04-15 | 109/140 | Classroom 109 Sink | Faucet | Initial | 5.97 | 2021-06-15
KN-01-BT-IN-NO-T | 63 | 2021-04-15 | 110/136 | Nurse's Office Restroom Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-01-RM-IN-NO-T | 64 | 2021-04-15 | 110/136 | Nurse's Office Sink | Faucet | Initial | 9.66 | 2021-06-15
KN-01-CR-IN-111-B | 20 | 2022-10-12 | 111/141 | Classroom 111 Bubbler | Bubbler | Initial | 6 | 2022-11-01 | New From Renovation
KN-01-CR-IN-111-T | 21 | 2022-10-12 | 111/141 | Classroom 111 Sink | Faucet | Initial | 5.9 | 2022-11-01 | New From Renovation
KN-01-CR-IN-111-T | 61 | 2021-04-15 | 111/141 | Classroom 111 Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-01-CR-IN-112-B | 18 | 2022-10-12 | 112/147 | Classroom 112 Bubbler | Bubbler | Initial | <5.00 | 2022-11-01 | New From Renovation
KN-01-CR-IN-112-T | 19 | 2022-10-12 | 112/147 | Classroom 112 Sink | Faucet | Initial | <5.00 | 2022-11-01 | New From Renovation
KN-01-CR-IN-112-T | 48 | 2021-04-15 | 112/147 | Room 112 Sink | Faucet | Initial | 5.57 | 2021-06-15
KN-01-RM-IN-MO-T | 47 | 2021-04-15 | 113C/145 | Sink in Main Office Room | Faucet | Initial | <5.00 | 2021-06-15
KN-01-CR-IN-114-T1 | 1 | 2022-10-12 | 114/180 | Classroom 114 (Art Room) Left Sink | Faucet | Initial | <5.00 | 2022-11-01 | New From Renovation
KN-01-CR-IN-114-T2 | 2 | 2022-10-12 | 114/180 | Classroom 114 (Art Room) Right Sink | Faucet | Initial | <5.00 | 2022-11-01 | New From Renovation
KN-01-CR-IN-114-T1 | 38 | 2021-04-15 | 114/180 | Classroom 114 Left Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-01-CR-IN-114-T2 | 39 | 2021-04-15 | 114/180 | Classroom 114 Right Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-01-CR-IN-116-BF | 12 | 2022-10-12 | 116/148 | Classroom 116 Bottle Filler | Bottle Filler | Initial | <5.00 | 2022-11-01
KN-01-CR-IN-116-T | 55 | 2021-04-15 | 116/148 | Classroom 116 Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-01-CR-IN-118-BF | 13 | 2022-10-12 | 118/149 | Classroom 118 Bottle Filler | Bottle Filler | Initial | <5.00 | 2022-11-01
KN-01-CR-IN-118-T | 56 | 2021-04-15 | 118/149 | Classroom 118 Sink | Faucet | Initial | 6.6 | 2021-06-15
KN-01-CR-IN-120-BF | 14 | 2022-10-12 | 120/150 | Classroom 120 Bottle Filler | Bottle Filler | Initial | 7.32 | 2022-11-01
KN-01-CR-IN-120-T | 59 | 2021-04-15 | 120/150 | Classroom 120 Sink | Faucet | Initial | 5.19 | 2021-06-15
KN-01-CR-IN-121-BF | 15 | 2022-10-12 | 121/153 | Classroom 121 Bottle Filler | Bottle Filler | Initial | <5.00 | 2022-11-01
KN-01-CR-IN-121-T | 57 | 2021-04-15 | 121/153 | Classroom 121 Sink | Faucet | Initial | 6.95 | 2021-06-15
KN-01-CR-IN-122-BF | 16 | 2022-10-12 | 122/151 | Classroom 122 Bottle Filler | Bottle Filler | Initial | <5.00 | 2022-11-01
KN-01-CR-IN-122-T | 60 | 2021-04-15 | 122/151 | Classroom 122 Sink | Faucet | Initial | 8.19 | 2021-06-15
KN-01-CR-IN-123-BF | 17 | 2022-10-12 | 123/152 | Classroom 123 Bottle Filler | Bottle Filler | Initial | <5.00 | 2022-11-01
KN-01-CR-IN-123-T | 58 | 2021-04-15 | 123/152 | Classroom 123 Sink | Faucet | Initial | 9.31 | 2021-06-15
KN-01-LR-IN-GLR-DF | 11 | 2022-10-12 | 126A | Girl's Locker Room Drinking Fountain | Drinking Fountain | Initial | 7.1 | 2022-11-01
KN-01-RM-IN-BLR-T | 41 | 2021-04-15 | 127/195 | Boys Locker Room Sink | Faucet | Initial | 5.62 | 2021-06-15
KN-01-BLR-IN-BLR-B | 1 | 2022-12-28 | 127/195 | Boys Locker Room Bubbler | Bubbler | Initial | 5 | 2023-01-05
KN-01-BT-IN-MLR-T | 42 | 2021-04-15 | 127A | Male Phys Ed Teacher's Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-01-OFF-IN-VPO-T | 10 | 2022-10-12 | 128/177 | Vice Principal's Office Sink | Faucet | Initial | <5.00 | 2022-11-01 | New From Renovation
KN-01-RM-IN-VP-T | 43 | 2021-04-15 | 128/177 | Vice Principal's Office Sink | Faucet | Initial | 5.41 | 2021-06-15
KN-01-FAC-IN-VPO-T | 1 | 2022-12-28 | 128/177 | Vice Principal's Office Sink | Faucet | Initial | 2 | 2023-01-05 | New fixture. Sampled 12/28/22
KN-01-RM-IN-LI-T | 40 | 2021-04-15 | 129/174 | Library Sink | Faucet | Initial | 34.1 | 2021-06-15 | WO#149108 - 7/19/2021. Replaced fittings. 2 - 1/2" 45. 3 - 1/2" 90. 1 - 1/2" gate valve. 1 - new faucet.
KN-01-RM-IN-LI-T | 33 | 2021-08-06 | 129/174 | Library Sink | Faucet | Post Remediation | 7.75 | 2021-08-13
KN-01-MC-IN-MC-T | 3 | 2022-03-31 | 129/174 | Sink in Media Center | Faucet | Initial | <5.00 | 2022-04-12 | New faucet install from library renovation
KN-02-GT-BY-TL-T | 17 | 2021-04-15 | 199A | Faculty Women's Room Sink By Teacher's Lounge (Right) | Faucet | Initial | 10.7 | 2021-06-15
KN-02-BT-BY-TL-T | 18 | 2021-04-15 | 199B | Faculty Men's Room Sink By Teacher's Lounge (Left) | Faucet | Initial | <5.00 | 2021-06-15
KN-02-CR-IN-201-B | 3 | 2022-02-23 | 201/200 | Classroom 201 Bubbler | Bubbler | Initial | 21.1 | 2022-03-08
KN-02-CR-IN-201-B | 1 | 2022-03-31 | 201/200 | Classroom 201 Bubbler | Bubbler | Post Remediation | 14.6 | 2022-04-12
KN-01-BT-BY-116-T3 | 50 | 2021-04-15 | Boys Restroom Near 116 | Boys Restroom Near Classroom 116 Right Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-01-BT-BY-116-T2 | 52 | 2021-04-15 | Boys Restroom Near 116 | Boys Restroom Near Classroom 116 Middle Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-01-BT-BY-116-T1 | 54 | 2021-04-15 | Boys Restroom Near 116 | Boys Restroom Near Classroom 116 Left Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-02-RM-BY-212-T | 37 | 2021-04-15 | Centum 6 Sink | Sink Near Room 212 | Faucet | Initial | 7.17 | 2021-06-15
KN-01-GT-BY-116-T1 | 49 | 2021-04-15 | Girls Restroom Near 116 | Girls Restroom Near Classroom 116 Left Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-01-GT-BY-116-T2 | 51 | 2021-04-15 | Girls Restroom Near 116 | Girls Restroom Near Classroom 116 Middle Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-01-GT-BY-116-T3 | 53 | 2021-04-15 | Girls Restroom Near 116 | Girls Restroom Near Classroom 116 Right Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-02-HA-BY-202-BF | 22 | 2021-04-15 | Hall between T3 and T4 | Bottle Filler Near Room 202 | Bottle Filler | Initial | <5.00 | 2021-06-15
KN-01-CR-BY-108-DF | 4 | 2022-02-23 | Hall Near 108/135 | Hallway by Classroom 108 Drinking Fountain | Drinking Fountain | Initial | <5.00 | 2022-03-08
KN-01-CR-BY-108-BF | 5 | 2022-02-23 | Hall Near 108/135 | Hallway by Classroom 108 Bottle Filler | Bottle Filler | Initial | <5.00 | 2022-03-08
KN-02-HA-BY-202-DF | 2 | 2022-03-31 | Hall Near 202 | Drinking Fountain Near Room 202 | Drinking Fountain | Initial | <5.00 | 2022-04-12
KN-01-HA-BY-MO-BF | 44 | 2021-04-15 | Hall Near Main Office | Bottle Filler Near Main Office | Bottle Filler | Initial | <5.00 | 2021-06-15
KN-01-HA-BY-MO-DF | 4 | 2022-03-31 | Hall Near Main Office | Drinking Fountain Near Main Office | Drinking Fountain | Initial | <5.00 | 2022-04-12
KN-02-GT-BY-202-T3 | 19 | 2021-04-15 | T3 Restroom | Girls Restroom Near Room 202 Right Sink | Faucet | Initial | 6.16 | 2021-06-15
KN-02-GT-BY-202-T2 | 20 | 2021-04-15 | T3 Restroom | Girls Restroom Near Room 202 Middle Sink | Faucet | Initial | 6.19 | 2021-06-15
KN-02-GT-BY-202-T1 | 21 | 2021-04-15 | T3 Restroom | Girls Restroom Near Room 202 Left Sink | Faucet | Initial | 8.39 | 2021-06-15
KN-02-BT-BY-202-T1 | 23 | 2021-04-15 | T4 Restroom | Boys Restroom Near Room 202 Left Sink | Faucet | Initial | 10.6 | 2021-06-15
KN-02-BT-BY-202-T2 | 24 | 2021-04-15 | T4 Restroom | Boys Restroom Near Room 202 Middle Sink | Faucet | Initial | 17.9 | 2021-06-15 | WO#149104 - 7/19/2021, Flush and change aerator.
KN-02-BT-BY-202-T2 | 29 | 2021-08-06 | T4 Restroom | Boys Restroom Near Room 202 Middle Sink | Faucet | Post Remediation | 24.8 | 2021-08-13
KN-02-BT-BY-202-T3 | 25 | 2021-04-15 | T4 Restroom | Boys Restroom Near Room 202 Right Sink | Faucet | Initial | 17.1 | 2021-06-15 | WO#149105 - 7/19/2021, Flush and change aerator.
KN-02-BT-BY-202-T3 | 30 | 2021-08-06 | T4 Restroom | Boys Restroom Near Room 202 Right Sink | Faucet | Post Remediation | 11 | 2021-08-13
KN-02-GT-BY-212-T2 | 34 | 2021-04-15 | T5 Girls Restroom | Girls Restroom Near Room 212 Right Sink | Faucet | Initial | 13.7 | 2021-06-15
KN-02-GT-BY-212-T1 | 36 | 2021-04-15 | T5 Girls Restroom | Girls Restroom Near Room 212 Left Sink | Faucet | Initial | 9.62 | 2021-06-15
KN-02-BT-BY-212-T1 | 33 | 2021-04-15 | T6 Boys Restroom | Boys Restroom Near Room 212 Left Sink | Faucet | Initial | 8.24 | 2021-06-15
KN-02-BT-BY-212-T2 | 35 | 2021-04-15 | T6 Boys Restroom | Boys Restroom Near Room 212 Right Sink | Faucet | Initial | 14.3 | 2021-06-15
KN-00-GT-BY-ART-T1 | 2 | 2021-04-15 | T7 Restroom | Girls Restroom Near Old Art Room Left Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-00-GT-BY-ART-T2 | 4 | 2021-04-15 | T7 Restroom | Girls Restroom Near Old Art Room Middle Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-00-GT-BY-ART-T3 | 6 | 2021-04-15 | T7 Restroom | Girls Restroom Near Old Art Room Right Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-00-BT-BY-ART-T3 | 3 | 2021-04-15 | T8 Restroom | Boys Restroom Near Old Art Room Right Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-00-BT-BY-ART-T2 | 5 | 2021-04-15 | T8 Restroom | Boys Restroom Near Old Art Room Middle Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-00-BT-BY-ART-T1 | 7 | 2021-04-15 | T8 Restroom | Boys Restroom Near Old Art Room Left Sink | Faucet | Initial | <5.00 | 2021-06-15
KN-00-BT-IN-KI-T | 12 | 2021-04-15 | T9 Restroom | Kitchen Restroom Sink | Faucet | Initial | <5.00 | 2021-06-15

## State Road
Date Last Updated |  | 2023-01-12
School Name: |  | State Road Elementary School
Lab ELAP ID# |  | NY63556 |  |  |  | Method of Analysis: |  |  | Metals 200.9
Lab ID# | School Sample ID # | Collection Date | Sample Location | Sample Location Description | Outlet Description | Initial/ Post Remediation | Lead Result mcg/L (ppb) | Lab Report Reciept Date | Action Taken for Outlets Greater than 15 mcg/L
SR-00-CR-IN-ART-T1 | 9 | 2021-04-20 | 11 | Art Room Left Sink (Moving Counterclockwise) | Faucet | Initial | <5.00 | 2021-06-15
SR-00-CR-IN-ART-T2 | 8 | 2021-04-20 | 11 | Art Room Middle Sink (Moving Counterclockwise) | Faucet | Initial | <5.00 | 2021-06-15
SR-00-CR-IN-ART-T3 | 7 | 2021-04-20 | 11 | Art Room Right Sink (Moving Counterclockwise) | Faucet | Initial | <5.00 | 2021-06-15
SR-01-CR-IN-104-T | 69 | 2021-04-20 | 14 | Classroom 104 Sink | Faucet | Initial | 12.7 | 2021-06-15
SR-00-RM-IN-KI-T3 | 12 | 2021-04-20 | 17 | Kitchen Sink 3 (Moving Clockwise) | Faucet | Initial | 11.8 | 2021-06-15
SR-00-RM-IN-KI-T1 | 10 | 2021-04-20 | 17 | Kitchen Sink 1 (Moving Clockwise) | Faucet | Initial | <5.00 | 2021-06-15
SR-00-RM-IN-KI-T2 | 11 | 2021-04-20 | 17 | Kitchen Sink 2 (Moving Clockwise) | Faucet | Initial | <5.00 | 2021-06-15
SR-00-RM-IN-KI-T4 | 13 | 2021-04-20 | 17 | Kitchen Sink 4 (Moving Clockwise) | Faucet | Initial | <5.00 | 2021-06-15
SR-00-RM-IN-CF-T | 15 | 2021-04-20 | 19 | Cafeteria Sink | Faucet | Initial | <5.00 | 2021-06-15
SR-00-RM-IN-CF-BF | 2 | 2022-02-24 | 19 | Cafeteria Bottle Filler | Bottle Filler | Initial | <5.00 | 2022-03-08
SR-00-RM-IN-CF-DF | 1 | 2022-02-24 | 19 | Cafeteria Drinking Fountain | Drinking Fountain | Initial | <5.00 | 2022-03-08
SR-01-BT-IN-101-T | 71 | 2021-04-20 | 101 | Classroom 101 Bathroom Sink | Faucet | Initial | 9.96 | 2021-06-15
SR-01-CR-IN-101-T | 72 | 2021-04-20 | 101 | Classroom 101 Sink | Faucet | Initial | 10.9 | 2021-06-15
SR-01-CR-IN-101-B | 6 | 2022-02-24 | 101 | Classroom 101 Bubbler | Bubbler | Initial | 6.35 | 2022-03-08
SR-01-CR-IN-101-BF | 31 | 2022-09-22 | 101 | Classroom 101 Bottle Filler | Bottle Filler | Initial | 51 | 2022-10-05
SR-01-CR-IN-101-BF-R | 1 | 2022-10-18 | 101 | Classroom 101 Bottle Filler RETEST | Bottle Filler | Post Remediation | <5.00 | 2022-11-01
SR-01-BT-IN-102-T | 73 | 2021-04-20 | 102 | Classroom 102 Bathroom Sink | Faucet | Initial | 13.8 | 2021-06-15
SR-01-CR-IN-102-T | 74 | 2021-04-20 | 102 | Classroom 102 Sink | Faucet | Initial | 20.1 | 2021-06-15 | WO#149114 - 7/24/2021. Hot and cold water lines were backwards, switched lines and flushed.
SR-01-CR-IN-102-T | 7 | 2021-08-11 | 102 | Classroom 102 Sink | Faucet | Post Remediation | 10.8 | 2021-08-23
SR-01-CR-IN-102-B | 7 | 2022-02-24 | 102 | Classroom 102 Bubbler | Bubbler | Initial | 9.78 | 2022-03-08
SR-01-CR-IN-102-B | 30 | 2022-09-22 | 102 | Classroom 102 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05 | New Fixture - 2022 Renovations
SR-01-CR-IN-103-T | 70 | 2021-04-20 | 103 | Classroom 103 Sink | Faucet | Initial | 5.3 | 2021-06-15
SR-01-CR-IN-103-B | 26 | 2022-09-22 | 103 | Classroom 103 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05 | New Fixture - 2022 Renovations
SR-01-CR-IN-103-T | 27 | 2022-09-22 | 103 | Classroom 103 Sink | Faucet | Initial | <5.00 | 2022-10-05 | New Fixture - 2022 Renovations
SR-01-CR-IN-104-B | 28 | 2022-09-22 | 104 | Classroom 104 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05 | New Fixture - 2022 Renovations
SR-01-CR-IN-104-T | 29 | 2022-09-22 | 104 | Classroom 104 Sink | Faucet | Initial | <5.00 | 2022-10-05 | New Fixture - 2022 Renovations
SR-01-CR-IN-105-T | 68 | 2021-04-20 | 105 | Classroom 105 Sink | Faucet | Initial | <5.00 | 2021-06-15
SR-01-CR-IN-105-B | 22 | 2022-09-22 | 105 | Classroom 105 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05 | New Fixture - 2022 Renovations
SR-01-CR-IN-105-T | 23 | 2022-09-22 | 105 | Classroom 105 Sink | Faucet | Initial | <5.00 | 2022-10-05 | New Fixture - 2022 Renovations
SR-01-CR-IN-106-T | 67 | 2021-04-20 | 106 | Classroom 106 Sink | Faucet | Initial | 5.02 | 2021-06-15
SR-01-CR-IN-106-B | 24 | 2022-09-22 | 106 | Classroom 106 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05 | New Fixture - 2022 Renovations
SR-01-CR-IN-106-T | 25 | 2022-09-22 | 106 | Classroom 106 Sink | Faucet | Initial | <5.00 | 2022-10-05 | New Fixture - 2022 Renovations
SR-01-CR-IN-107-T | 66 | 2021-04-20 | 107 | Classroom 107 Sink | Faucet | Initial | <5.00 | 2021-06-15
SR-01-CR-IN-107-B | 20 | 2022-09-22 | 107 | Classroom 107 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05 | New Fixture - 2022 Renovations
SR-01-CR-IN-107-T | 21 | 2022-09-22 | 107 | Classroom 107 Sink | Faucet | Initial | <5.00 | 2022-10-05 | New Fixture - 2022 Renovations
SR-01-CR-IN-108-T | 65 | 2021-04-20 | 108 | Classroom 108 Sink | Faucet | Initial | 7.56 | 2021-06-15
SR-01-CR-IN-108-B | 18 | 2022-09-22 | 108 | Classroom 108 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05 | New Fixture - 2022 Renovations
SR-01-CR-IN-108-T | 19 | 2022-09-22 | 108 | Classroom 108 Sink | Faucet | Initial | <5.00 | 2022-10-05 | New Fixture - 2022 Renovations
SR-01-CR-IN-109-T | 62 | 2021-04-20 | 109 | Classroom 109 Sink | Faucet | Initial | 7.55 | 2021-06-15
SR-01-CR-IN-109-B | 16 | 2022-09-22 | 109 | Classroom 109 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05 | New Fixture - 2022 Renovations
SR-01-CR-IN-109-T | 17 | 2022-09-22 | 109 | Classroom 109 Sink | Faucet | Initial | <5.00 | 2022-10-05 | New Fixture - 2022 Renovations
SR-01-RM-IN-NO-T | 64 | 2021-04-20 | 110 | Nurse's Office Sink | Faucet | Initial | 7.5 | 2021-06-15
SR-01-BT-IN-NO-T | 63 | 2021-04-20 | 110 | Nurse's Office Restroom Sink | Faucet | Initial | <5.00 | 2021-06-15
SR-01-CR-IN-111-T | 61 | 2021-04-20 | 111 | Classroom 111 Sink | Faucet | Initial | 5.33 | 2021-06-15
SR-01-CR-IN-111-B | 14 | 2022-09-22 | 111 | Classroom 111 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05 | New Fixture - 2022 Renovations
SR-01-CR-IN-111-T | 15 | 2022-09-22 | 111 | Classroom 111 Sink | Faucet | Initial | <5.00 | 2022-10-05 | New Fixture - 2022 Renovations
SR-01-CR-IN-112-T | 49 | 2021-04-20 | 112 | Room 112 Sink | Faucet | Initial | <5.00 | 2021-06-15
SR-01-CR-IN-112-B | 12 | 2022-09-22 | 112 | Classroom 112 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05 | New Fixture - 2022 Renovations
SR-01-CR-IN-112-T | 13 | 2022-09-22 | 112 | Classroom 112 Sink | Faucet | Initial | <5.00 | 2022-10-05 | New Fixture - 2022 Renovations
SR-01-CR-IN-114-T | 40 | 2021-04-20 | 114 | Sink In Classroom 114 | Faucet | Initial | <5.00 | 2021-06-15
SR-01-CR-IN141-TL | 8 | 2022-09-22 | 114 | Classroom 114 Faucet - Left | Faucet | Initial | <5.00 | 2022-10-05 | New Fixture - 2022 Renovations
SR-01-CR-IN141-TR | 9 | 2022-09-22 | 114 | Classroom 114 Faucet - Right | Faucet | Initial | <5.00 | 2022-10-05 | New Fixture - 2022 Renovations
SR-01-RM-IN-115-T | 44 | 2021-04-20 | 115 | Room 115 Sink | Faucet | Initial | 11.9 | 2021-06-15
SR-01-CR-IN-118-T | 56 | 2021-04-20 | 118 | Classroom 118 Sink | Faucet | Initial | 14.2 | 2021-06-15
SR-01-CR-IN-118-BF | 32 | 2022-09-22 | 118 | Classroom 118 Bottle Filler | Bottle Filler | Initial | 13.5 | 2022-10-05
SR-01-CR-IN-120-T | 59 | 2021-04-20 | 120 | Classroom 120 Sink | Faucet | Initial | 10.4 | 2021-06-15
SR-01-CR-IN-120-BF | 33 | 2022-09-22 | 120 | Classroom 120 Bottle Filler | Bottle Filler | Initial | <5.00 | 2022-10-05
SR-01-CR-IN-121-T | 57 | 2021-04-20 | 121 | Classroom 121 Sink | Faucet | Initial | 26 | 2021-06-15 | WO#149113 - 7/24/2021. Replaced fittings. 1 - 1/2" 90, 1 - 1/2" gate valve, 1 - 1/2" x 3/8" compression, 1 - chrome stop.
SR-01-CR-IN-121-T | 6 | 2021-08-11 | 121 | Classroom 121 Sink | Faucet | Post Remediation | 6.96 | 2021-08-23
SR-01-CR-121-BF | 34 | 2022-09-22 | 121 | Classroom 121 Bottle Filler | Bottle Filler | Initial | 18.1 | 2022-10-05
SR-01-CR-IN-121-BF-R | 2 | 2022-10-18 | 121 | Classroom 121 Bottle Filler RETEST | Bottle Filler | Post Remediation | <5.00 | 2022-11-01
SR-01-CR-IN-122-T | 60 | 2021-04-20 | 122 | Classroom 122 Sink | Faucet | Initial | 9.55 | 2021-06-15
SR-01-CR-IN-122-BF | 35 | 2022-09-22 | 122 | Classroom 122 Bottle Filler | Bottle Filler | Initial | <5.00 | 2022-10-05
SR-01-CR-IN-123-T | 58 | 2021-04-20 | 123 | Classroom 123 Sink | Faucet | Initial | 8.29 | 2021-06-15
SR-01-CR-IN-123-BF | 36 | 2022-09-22 | 123 | Classroom 123 Bottle Filler | Bottle Filler | Initial | <5.00 | 2022-10-05
SR-01-RM-IN-LI-T | 41 | 2021-04-20 | 129 | Library Sink | Faucet | Initial | 47.2 | 2021-06-15 | WO#149111 - 7/27/2021. Replaced fittings. 1 - 1/2" gate valve, 1 - 1/2" x 3/8" compression, 4 - 90s.
SR-01-RM-IN-LI-T | 4 | 2021-08-11 | 129 | Library Sink | Faucet | Post Remediation | <5.00 | 2021-08-23
SR-01-RM-IN-LIB-T | 3 | 2022-04-01 | 129 | Sink in Library | Faucet | Initial | 5.11 | 2022-04-12 | New fixture from Library renovation
SR-02-RM-IN-TL-T | 17 | 2021-04-20 | 199 | 2nd Floor Teacher's Lounge Sink | Faucet | Initial | 5.41 | 2021-06-15
SR-02-CR-IN-201-T | 16 | 2021-04-20 | 201 | Room 201 Sink | Faucet | Initial | <5.00 | 2021-06-15
SR-02-CR-IN-201-B | 3 | 2022-02-24 | 201 | Room 201 Bubbler | Bubbler | Initial | 6.82 | 2022-03-08
SR-02-CR-IN-202-T | 27 | 2021-04-20 | 202 | Classroom 202 Sink | Faucet | Initial | 11.7 | 2021-06-15
SR-02-HA-BY-202-DF | 1 | 2022-04-01 | 202 | Drinking Fountain by 202 | Drinking Fountain | Initial | <5.00 | 2022-04-12
SR-02-CR-IN-202-B | 1 | 2022-09-22 | 202 | Classroom 202 Bubbler | Bubbler | Initial | 15.5 | 2022-10-05
SR-02-CR-IN-202-B-R | 3 | 2022-10-18 | 202 | Classroom 202 Bubbler RETEST | Bubbler | Post Remediation | 8.73 | 2022-11-01
SR-02-CR-IN-204-T | 29 | 2021-04-20 | 204 | Classroom 204 Sink | Faucet | Initial | 6.93 | 2021-06-15
SR-02-CR-IN-204-B | 2 | 2022-09-22 | 204 | Classroom 204 Bubbler | Bubbler | Initial | 7.37 | 2022-10-05
SR-02-CR-IN-205-T | 28 | 2021-04-20 | 205 | Classroom 205 Sink | Faucet | Initial | 18.7 | 2021-06-15 | WO#149110 - 7/24/2021. Replaced fittings. 1 - 1/2" chrome stop, 1 - 3/8" brass T, 1 - 1/2" coupler, 1 - 1/2" 90.
SR-02-CR-IN-205-T | 2 | 2021-08-11 | 205 | Classroom 205 Sink | Faucet | Post Remediation | 12.7 | 2021-08-23
SR-02-CR-IN-205-B | 3 | 2022-09-22 | 205 | Classroom 205 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
SR-02-CR-IN-206-T | 31 | 2021-04-20 | 206 | Classroom 206 Sink | Faucet | Initial | <5.00 | 2021-06-15
SR-02-CR-IN-206-B | 4 | 2022-09-22 | 206 | Classroom 206 Bubbler | Bubbler | Initial | 28.1 | 2022-10-05
SR-02-CR-IN-206-B-R | 4 | 2022-10-18 | 206 | Classroom 206 Bubbler RETEST | Bubbler | Post Remediation | 12.3 | 2022-11-01
SR-02-CR-IN-207-T | 30 | 2021-04-20 | 207 | Classroom 207 Sink | Faucet | Initial | 7.76 | 2021-06-15
SR-02-CR-IN-207-B | 5 | 2022-09-22 | 207 | Classroom 207 Bubbler | Bubbler | Initial | 5.36 | 2022-10-05
SR-02-CR-IN-208-T | 33 | 2021-04-20 | 208 | Classroom 208 Sink | Faucet | Initial | 5.46 | 2021-06-15
SR-02-CR-IN-208-B | 6 | 2022-09-22 | 208 | Classroom 208 Bubbler | Bubbler | Initial | 9.04 | 2022-10-05
SR-02-CR-IN-209-T | 32 | 2021-04-20 | 209 | Classroom 209 Sink | Faucet | Initial | 5.91 | 2021-06-15
SR-02-CR-IN-209-B | 7 | 2022-09-22 | 209 | Classroom 209 Bubbler | Bubbler | Initial | 6.89 | 2022-10-05
SR-01-CR-IN-210B-T | 3 | 2022-12-28 | 210B | Classroom 210B Tap | Faucet | Initial | 10 | 2023-01-05 | Sampled 12/28/22
SR-01-CR-IN-210B-BF | 4 | 2022-12-28 | 210B | Classroom 214 Bottle Filler | Bottle Filler | Initial | 8 | 2023-01-05 | Sampled 12/28/22
SR-01-CR-IN-214-T | 1 | 2022-12-28 | 214 | Classroom 214 Tap | Faucet | Initial | 9 | 2023-01-05 | Sampled 12/28/22
SR-01-CR-IN-214-B | 2 | 2022-12-28 | 214 | Classroom 214 Bubbler | Bubbler | Initial | 8 | 2023-01-05 | Sampled 12/28/22
SR-01-RM-IN-MO-T | 48 | 2021-04-20 | 113C | Sink in Main Office Room | Faucet | Initial | <5.00 | 2021-06-15
SR-01-LOC-IN-GLR-DF | 11 | 2022-09-22 | 126A | Girl's Locker Room Drinking Fountain | Drinking Fountain | Initial | <5.00 | 2022-10-05
SR-01-RM-IN-GLR-T | 47 | 2021-04-20 | 126D | Girls Locker Room Sink | Faucet | Initial | <5.00 | 2021-06-15
SR-01-LOC-IN-BLR-DF | 10 | 2022-09-22 | 127A | Boy's Locker Room Drinking Fountain | Drinking Fountain | Initial | 5.6 | 2022-10-05
SR-01-BT-IN-MLR-T | 43 | 2021-04-20 | 127B | Male Phys Ed Teacher's Sink | Faucet | Initial | 10.5 | 2021-06-15
SR-01-BT-IN-BLR-T | 42 | 2021-04-20 | 127C | Boys Locker Room Sink | Faucet | Initial | 16.1 | 2021-06-15 | WO#149112 - 7/27/2021. Flush and install new aerator.
SR-01-BT-IN-BLR-T | 5 | 2021-08-11 | 127C | Boys Locker Room Sink | Faucet | Post Remediation | 8.89 | 2021-08-23
SR-01-GT-IN-WLR-T | 46 | 2021-04-20 | 17G | Female Phys Ed Teacher's Sink | Faucet | Initial | <5.00 | 2021-06-15
SR-02-GT-BY-TL-T | 18 | 2021-04-20 | 199A | Faculty Women's Room Sink By Teacher's Lounge (Right) | Faucet | Initial | 6.49 | 2021-06-15
SR-02-BT-BY-TL-T | 19 | 2021-04-20 | 199B | Faculty Men's Room Sink By Teacher's Lounge (Right) | Faucet | Initial | 45.1 | 2021-06-15 | WO#149109 - 7/27/2021. Flush and install new aerator.
SR-02-BT-BY-TL-T | 1 | 2021-08-11 | 199B | Faculty Men's Room Sink By Teacher's Lounge (Right) | Faucet | Post Remediation | 13.3 | 2021-08-23
SR-02-RM-BY-211-T2 | 38 | 2021-04-20 | Centum 6 Sink | Right Sink Near Room 211 | Faucet | Initial | 6.18 | 2021-06-15
SR-02-RM-BY-211-T1 | 39 | 2021-04-20 | Centum 6 Sink | Left Sink Near Room 211 | Faucet | Initial | 8.73 | 2021-06-15
SR-02-HA-BY-202-BF | 23 | 2021-04-20 | Hall between T3 and T4 | Bottle Filler Near Room 202 | Bottle Filler | Initial | <5.00 | 2021-06-15
SR-01-HA-BY-108-BF | 5 | 2022-02-24 | Hall by 108 | Hallway by 108 Bottle Filler | Bottle Filler | Initial | <5.00 | 2022-03-08
SR-01-HA-BY-108-DF | 4 | 2022-02-24 | Hall by 108 | Hallway by 108 Drinking Fountain | Drinking Fountain | Initial | <5.00 | 2022-03-08
SR-02-HA-BY-210-BF | 3 | 2021-08-11 | Hall by 210 | Bottle Filler by Room 210 | Bottle Filler | Initial | <5.00 | 2021-08-23
SR-01-HA-BY-MO-DF | 2 | 2022-04-01 | Hall by Main Office | Drinking Fountain by Main Office | Drinking Fountain | Initial | <5.00 | 2022-04-12
SR-01-HA-BY-MO-BF | 45 | 2021-04-20 | Hall Near Main Office | Bottle Filler Near Main Office | Bottle Filler | Initial | <5.00 | 2021-06-15
SR-01-GT-BY-116-T1 | 50 | 2021-04-20 | T1 Restroom | Girls Restroom Near Classroom 116 Left Sink | Faucet | Initial | <5.00 | 2021-06-15
SR-01-GT-BY-116-T2 | 52 | 2021-04-20 | T1 Restroom | Girls Restroom Near Classroom 116 Middle | Faucet | Initial | <5.00 | 2021-06-15
SR-01-GT-BY-116-T3 | 54 | 2021-04-20 | T1 Restroom | Girls Restroom Near Classroom 116 Right Sink | Faucet | Initial | <5.00 | 2021-06-15
SR-01-BT-BY-116-T1 | 55 | 2021-04-20 | T2 Restroom | Boys Restroom Near Classroom 116 Left Sink | Faucet | Initial | <5.00 | 2021-06-15
SR-01-BT-BY-116-T2 | 53 | 2021-04-20 | T2 Restroom | Boys Restroom Near Classroom 116 Middle | Faucet | Initial | <5.00 | 2021-06-15
SR-01-BT-BY-116-T3 | 51 | 2021-04-20 | T2 Restroom | Boys Restroom Near Classroom 116 Right Sink | Faucet | Initial | <5.00 | 2021-06-15
SR-02-GT-BY-202-T1 | 22 | 2021-04-20 | T3 Girls Restroom | Girls Restroom Near Room 202 Left Sink | Faucet | Initial | <5.00 | 2021-06-15
SR-02-GT-BY-202-T2 | 21 | 2021-04-20 | T3 Girls Restroom | Girls Restroom Near Room 202 Middle Sink | Faucet | Initial | <5.00 | 2021-06-15
SR-02-GT-BY-202-T3 | 20 | 2021-04-20 | T3 Girls Restroom | Girls Restroom Near Room 202 Right Sink | Faucet | Initial | <5.00 | 2021-06-15
SR-02-BT-BY-202-T1 | 24 | 2021-04-20 | T4 Restroom | Boys Restroom Near Room 202 Left Sink | Faucet | Initial | 11.7 | 2021-06-15
SR-02-BT-BY-202-T2 | 25 | 2021-04-20 | T4 Restroom | Boys Restroom Near Room 202 Middle Sink | Faucet | Initial | <5.00 | 2021-06-15
SR-02-BT-BY-202-T3 | 26 | 2021-04-20 | T4 Restroom | Boys Restroom Near Room 202 Right Sink | Faucet | Initial | <5.00 | 2021-06-15
SR-02-GT-BY-211-T2 | 35 | 2021-04-20 | T5 Restroom | Girls Restroom Near Room 211 Right Sink | Faucet | Initial | 5.03 | 2021-06-15
SR-02-BT-BY-211-T2 | 36 | 2021-04-20 | T5 Restroom | Boys Restroom Near Room 211 Right Sink | Faucet | Initial | <5.00 | 2021-06-15
SR-02-GT-BY-211-T1 | 37 | 2021-04-20 | T6 Restroom | Girls Restroom Near Room 211 Left Sink | Faucet | Initial | 6.47 | 2021-06-15
SR-02-BT-BY-211-T1 | 34 | 2021-04-20 | T6 Restroom | Boys Restroom Near Room 211 Left Sink | Faucet | Initial | 12.8 | 2021-06-15
SR-00-GT-BY-ART-T3 | 5 | 2021-04-20 | T7 Restroom | Girls Restroom Near Art Room Right Hand Sink | Faucet | Initial | 7.24 | 2021-06-15
SR-00-GT-BY-ART-T1 | 1 | 2021-04-20 | T7 Restroom | Girls Restroom Near Art Room Left Hand Sink | Faucet | Initial | <5.00 | 2021-06-15
SR-00-GT-BY-ART-T2 | 3 | 2021-04-20 | T7 Restroom | Girls Restroom Near Art Room Middle Sink | Faucet | Initial | <5.00 | 2021-06-15
SR-00-BT-BY-ART-T1 | 6 | 2021-04-20 | T8 Restroom | Boys Restroom Near Art Room Left Hand Sink | Faucet | Initial | <5.00 | 2021-06-15
SR-00-BT-BY-ART-T2 | 4 | 2021-04-20 | T8 Restroom | Boys Restroom Near Art Room Middle Sink | Faucet | Initial | <5.00 | 2021-06-15
SR-00-BT-BY-ART-T3 | 2 | 2021-04-20 | T8 Restroom | Boys Restroom Near Art Room Right Hand Sink | Faucet | Initial | <5.00 | 2021-06-15
SR-00-BT-IN-KI-T | 14 | 2021-04-20 | T9 Restroom | Kitchen Bathroom Sink | Faucet | Initial | <5.00 | 2021-06-15

## Dewitt Road
Date Last Updated |  | 2023-01-12
School Name: |  | Dewitt Road Elementary School
Lab ELAP ID# |  | NY63556 |  |  |  | Method of Analysis: |  |  | Metals 200.9
Lab ID# | School Sample ID # | Collection Date | Sample Location | Sample Location Description | Outlet Description | Initial/ Post Remediation | Lead Result mcg/L (ppb) | Lab Report Reciept Date | Action Taken for Outlets Greater than 15 mcg/L
DW-01-CR-IN-101-T | 28 | 2021-04-22 | 101 | Classroom 101 Tap | Faucet | Initial | 6.97 | 2021-06-15
DW-01-CR-IN-101-B | 7 | 10/12/2022 | 101 | Classroom 101 Bubbler | Bubbler | Initial | <5.00 | 2022-11-01
DW-01-CR-IN-102-T | 29 | 2021-04-22 | 102 | Classroom 102 Tap | Faucet | Initial | <5.00 | 2021-06-15
DW-01-CR-IN-102-B | 8 | 10/12/2022 | 102 | Classroom 102 Bubbler | Bubbler | Initial | <5.00 | 2022-11-01
DW-01-CR-IN-103-T | 4 | 2021-04-22 | 103 | Classroom 103 Tap | Faucet | Initial | <5.00 | 2021-06-15
DW-01-CR-IN-103-B | 4 | 10/12/2022 | 103 | Classroom 103 Bubbler | Bubbler | Initial | <5.00 | 2022-11-01
DW-01-CR-IN-104-T | 3 | 2021-04-22 | 104 | Classroom 104 Tap | Faucet | Initial | <5.00 | 2021-06-15
DW-01-CR-IN-104-B | 3 | 10/12/2022 | 104 | Classroom 104 Bubbler | Bubbler | Initial | <5.00 | 2022-11-01
DW-01-CR-IN-105-T | 2 | 2021-04-22 | 105 | Classroom 105 Tap | Faucet | Initial | <5.00 | 2021-06-15
DW-01-CR-IN-105-B | 2 | 10/12/2022 | 105 | Classroom 105 Bubbler | Bubbler | Initial | <5.00 | 2022-11-01
DW-01-CR-IN-106-T | 1 | 2021-04-22 | 106 | Classroom 106 Tap | Faucet | Initial | <5.00 | 2021-06-15
DW-01-RM-IN-106-T | 2 | 2021-10-01 | 106 | Classroom 106 Tap | Faucet | Initial | 14.9 | 2021-10-08 | New Faucet From Renovation
DW-01-CR-IN-106-B | 1 | 2022-02-23 | 106 | Classroom 106 Bubbler | Bubbler | Initial | 9.7 | 2022-03-08
DW-01-CR-IN-106-B | 1 | 10/12/2022 | 106 | Classroom 106 (Music Room) Bubbler | Bubbler | Initial | 5.18 | 2022-11-01 | New From Renovation
DW-01-RM-BY-111-T1 | 35 | 2021-04-22 | 111 | Left Tap Near Room 111 | Faucet | Initial | 9.65 | 2021-06-15
DW-01-RM-BY-111-T2 | 34 | 2021-04-22 | 111 | Right Tap Near Room 111 | Faucet | Initial | 8.82 | 2021-06-15
DW-01-CR-IN-117-T | 8 | 2021-04-22 | 117 | Classroom 117 Tap | Faucet | Initial | 5.35 | 2021-06-15
DW-01-CR-IN-117-BF | 5 | 10/12/2022 | 117 | Classroom 117 Bottle Filler | Bottle Filler | Initial | <5.00 | 2022-11-01
DW-01-CR-IN-118-T | 7 | 2021-04-22 | 118 | Classroom 118 Tap | Faucet | Initial | 5.33 | 2021-06-15
DW-01-CR-IN-118-BF | 6 | 10/12/2022 | 118 | Classroom 118 Bottle Filler | Bottle Filler | Initial | <5.00 | 2022-11-01
DW-01-CR-IN-131-B | 2 | 2022-02-23 | 131 | Classroom 131 Bubbler | Bubbler | Initial | 8.1 | 2022-03-08
DW-02-RM-IN-201-T | 59 | 2021-04-23 | 201 | Room 201 Tap | Faucet | Initial | 8.48 | 2021-06-15
DW-02-RM-IN-201-T | 20 | 2021-10-01 | 201 | Room 201 Tap | Faucet | Initial | 8.23 | 2021-10-08 | New Faucet From Renovation
DW-02-CR-IN-202-T | 60 | 2021-04-23 | 202 | Classroom 202 Tap | Faucet | Initial | <5.00 | 2021-06-15
DW-02-CR-IN-202-T | 22 | 2021-10-01 | 202 | Classroom 202 Tap | Faucet | Initial | <5.00 | 2021-10-08 | New Faucet From Renovation
DW-02-CR-IN-202-B | 22 | 10/12/2022 | 202 | Classroom 202 Bubbler | Bubbler | Initial | <5.00 | 2022-11-01
DW-02-CR-IN-203-T | 61 | 2021-04-23 | 203 | Classroom 203 Tap | Faucet | Initial | 5.23 | 2021-06-15
DW-02-CR-IN-203-T | 23 | 2021-10-01 | 203 | Classroom 203 Tap | Faucet | Initial | <5.00 | 2021-10-08 | New Faucet From Renovation
DW-02-CR-IN-203-B | 21 | 10/12/2022 | 203 | Classroom 203 Bubbler | Bubbler | Initial | <5.00 | 2022-11-01
DW-02-CR-IN-204-T | 66 | 2021-04-23 | 204 | Classroom 204 Tap | Faucet | Initial | 10.2 | 2021-06-15
DW-02-CR-IN-204-T | 24 | 2021-10-01 | 204 | Classroom 204 Tap | Faucet | Initial | 14.2 | 2021-10-08 | New Faucet From Renovation
DW-02-CR-IN-204-B | 20 | 10/12/2022 | 204 | Classroom 204 Bubbler | Bubbler | Initial | 11.9 | 2022-11-01
DW-02-CR-IN-205-T | 53 | 2021-04-23 | 205 | Classroom 205 Tap | Faucet | Initial | 10.9 | 2021-06-15
DW-02-CR-IN-205-T | 17 | 2021-10-01 | 205 | Classroom 205 Tap | Faucet | Initial | 12.3 | 2021-10-08 | New Faucet From Renovation
DW-02-CR-IN-205-B | 19 | 10/12/2022 | 205 | Classroom 205 Bubbler | Bubbler | Initial | 12.7 | 2022-11-01
DW-02-CR-IN-206-T | 51 | 2021-04-23 | 206 | Classroom 206 Tap | Faucet | Initial | 7.41 | 2021-06-15
DW-02-CR-IN-206-T | 16 | 2021-10-01 | 206 | Classroom 206 Tap | Faucet | Initial | 8.09 | 2021-10-08 | New Faucet From Renovation
DW-02-CR-IN-206-B | 18 | 10/12/2022 | 206 | Classroom 206 Bubbler | Bubbler | Initial | 6.76 | 2022-11-01
DW-02-CR-IN-207-T | 50 | 2021-04-23 | 207 | Classroom 207 Tap | Faucet | Initial | 7.31 | 2021-06-15
DW-02-CR-IN-207-T | 15 | 2021-10-01 | 207 | Classroom 207 Tap | Faucet | Initial | 7.84 | 2021-10-08 | New Faucet From Renovation
DW-02-CR-IN-207-B | 17 | 10/12/2022 | 207 | Classroom 207 Bubbler | Bubbler | Initial | 7.96 | 2022-11-01
DW-02-CR-IN-208-T | 49 | 2021-04-23 | 208 | Classroom 208 Tap | Faucet | Initial | 11.5 | 2021-06-15
DW-02-CR-IN-208-T | 14 | 2021-10-01 | 208 | Classroom 208 Tap | Faucet | Initial | 14.4 | 2021-10-08 | New Faucet From Renovation
DW-02-CR-IN-208-B | 16 | 10/12/2022 | 208 | Classroom 208 Bubbler | Bubbler | Initial | 19.8 | 2022-11-01 | Replaced line, valve and bubbler
DW-02-CR-IN-208-DF | 1 | 2022-12-28 | 208 | Classroom 208 Drinking Fountain | Drinking Fountain | Post Remediation | 31 | 2023-01-05
DW-02-CR-IN-209-T | 48 | 2021-04-23 | 209 | Classroom 209 Tap | Faucet | Initial | <5.00 | 2021-06-15
DW-02-CR-IN-209-T | 13 | 2021-10-01 | 209 | Classroom 209 Tap | Faucet | Initial | 8.65 | 2021-10-08 | New Faucet From Renovation
DW-02-CR-IN-209-B | 15 | 10/12/2022 | 209 | Classroom 209 Bubbler | Bubbler | Initial | 5.49 | 2022-11-01
DW-02-CR-IN-210-T | 42 | 2021-04-23 | 210 | Classroom 210 Tap | Faucet | Initial | <5.00 | 2021-06-15
DW-02-CR-IN-210-T | 9 | 2021-10-01 | 210 | Classroom 210 Tap | Faucet | Initial | 7.01 | 2021-10-08 | New Faucet From Renovation
DW-02-CR-IN-210-B | 12 | 10/12/2022 | 210 | Classroom 210 Bubbler | Bubbler | Initial | 7.25 | 2022-11-01
DW-02-CR-IN-211-T | 38 | 2021-04-23 | 211 | Classroom 211 Tap | Faucet | Initial | 10.4 | 2021-06-15
DW-02-CR-IN-211-T | 8 | 2021-10-01 | 211 | Classroom 211 Tap | Faucet | Initial | 9.71 | 2021-10-08 | New Faucet From Renovation
DW-02-CR-IN-211-B | 11 | 10/12/2022 | 211 | Classroom 211 Bubbler | Bubbler | Initial | 10.2 | 2022-11-01
DW-02-CR-IN-212-T | 37 | 2021-04-23 | 212 | Classroom 212 Tap | Faucet | Initial | <5.00 | 2021-06-15
DW-02-CR-IN-212-T | 7 | 2021-10-01 | 212 | Classroom 212 Tap | Faucet | Initial | 6.96 | 2021-10-08 | New Faucet From Renovation
DW-02-CR-IN-212-B | 10 | 10/12/2022 | 212 | Classroom 212 Bubbler | Bubbler | Initial | 5.56 | 2022-11-01
DW-02-CR-IN-213-T | 36 | 2021-04-23 | 213 | Classroom 213 Tap | Faucet | Initial | <5.00 | 2021-06-15
DW-02-CR-IN-213-T | 6 | 2021-10-01 | 213 | Classroom 213 Tap | Faucet | Initial | 5.35 | 2021-10-08 | New Faucet From Renovation
DW-02-CR-IN-213-B | 9 | 10/12/2022 | 213 | Classroom 213 Bubbler | Bubbler | Initial | 5.91 | 2022-11-01
DW-02-CR-IN-214-T | 54 | 2021-04-23 | 214 | Classroom 214 Tap | Faucet | Initial | 6.8 | 2021-06-15
DW-02-CR-IN-214-T | 18 | 2021-10-01 | 214 | Classroom 214 Tap | Faucet | Initial | 10.4 | 2021-10-08 | New Faucet From Renovation
DW-02-CR-IN-214-B | 23 | 10/12/2022 | 214 | Classroom 214 Bubbler | Bubbler | Initial | 10.4 | 2022-11-01
DW-02-CR-IN-217-T | 46 | 2021-04-23 | 217 | Classroom 217 Tap | Faucet | Initial | <5.00 | 2021-06-15
DW-02-CR-IN-217-B | 5 | 2022-02-23 | 217 | Classroom 217 Bubbler | Bubbler | Initial | <5.00 | 2022-03-08
DW-02-CR-IN-217-B | 13 | 10/12/2022 | 217 | Classroom 217 Bubbler | Bubbler | Initial | 5.16 | 2022-11-01
DW-02-CR-IN-218-T | 45 | 2021-04-23 | 218 | Classroom 218 Tap | Faucet | Initial | 28.6 | 2021-06-15 | WO#149117 - 7/9/2021. Replaced fittings. 1 - 1/2" propress ball valve. 1 - 1/2" propress male adaptor. 1 - 1/2" propress T. 1 - 1/2"x3/8" stop. 1 - 1/2" propress 90 st. 2' 1/2" copper. 1 - 1/2" x 3/8" x 12" braided supply line
DW-02-CR-IN-218-T | 10 | 2021-10-01 | 218 | Classroom 218 Tap | Faucet | Post Remediation | <5.00 | 2021-10-08
DW-02-CR-IN-218-B | 14 | 10/12/2022 | 218 | Classroom 218 Bubbler | Bubbler | Initial | <5.00 | 2022-11-01
DW-01-RM-IN-TL-T | 19 | 2021-04-22 | 219 | Teachers Lounge Tap | Faucet | Initial | <5.00 | 2021-06-15
DW-02-RM-IN-LI-T | 21 | 2021-10-01 | 220 Library | Tap in Library | Faucet | Initial | <5.00 | 2021-10-08 | New Faucet From Renovation
DW-01-CR-IN-ART-T2 | 16 | 2021-04-22 | Art | Art Room Right Sink | Faucet | Initial | <5.00 | 2021-06-15
DW-01-CR-IN-ART-T1 | 17 | 2021-04-22 | Art | Art Room Left Sink | Faucet | Initial | <5.00 | 2021-06-15
DW-01-CR-IN-ART-T | 4 | 2021-10-01 | Art | 2-Art Room Right Sink | Faucet | Initial | <5.00 | 2021-10-08 | New Faucet From Renovation
DW-01-CR-IN-ART-T | 5 | 2021-10-01 | Art | 1-Art Room Right Sink | Faucet | Initial | <5.00 | 2021-10-08 | New Faucet From Renovation
DW-01-BT-IN-CAFÉ-T1 | 26 | 2021-04-22 | Boys Cafeteria Restroom | Boys Cafeteria Restroom Left Tap | Faucet | Initial | <5.00 | 2021-06-15
DW-01-BT-IN-CAFÉ-T2 | 27 | 2021-04-22 | Boys Cafeteria Restroom | Boys Cafeteria Restroom Right Tap | Faucet | Initial | <5.00 | 2021-06-15
DW-02-MLR-IN-GYM-T | 47 | 2021-04-23 | Boys PE Office | Male Phys Ed Teacher Restroom Tap | Faucet | Initial | 15.8 | 2021-06-15 | WO#149118 6/23/2021 - Flush and install new aerator.
DW-02-MLR-IN-GYM-T | 47 | 2021-10-01 | Boys PE Office | Male Phys Ed Teacher Restroom Tap | Faucet | Post Remediation | 9.61 | 2021-10-08
DW-01-BT-BY-111-T1 | 30 | 2021-04-22 | Boys Restroom by 111 | Boys Restroom By Room 111 Left Sink | Faucet | Initial | 8.08 | 2021-06-15
DW-01-BT-BY-111-T2 | 32 | 2021-04-22 | Boys Restroom by 111 | Boys Restroom By Room 111 Right Sink | Faucet | Initial | 5.82 | 2021-06-15
DW-02-BT-BY-209-T1 | 39 | 2021-04-23 | Boys Restroom By 209 | Boys Restroom Near Room 209 Left Tap | Faucet | Initial | <5.00 | 2021-06-15
DW-02-BT-BY-209-T2 | 40 | 2021-04-23 | Boys Restroom By 209 | Boys Restroom Near Room 209 Middle Tap | Faucet | Initial | <5.00 | 2021-06-15
DW-02-BT-BY-209-T3 | 41 | 2021-04-23 | Boys Restroom By 209 | Boys Restroom Near Room 209 Right Tap | Faucet | Initial | <5.00 | 2021-06-15
DW-01-RM-IN-CAFÉ-BF | 9 | 2021-04-22 | Cafeteria | Cafeteria Bottle Filler | Bottle Filler | Initial | <5.00 | 2021-06-15
DW-01-CAFÉ-IN-DF | 2 | 2022-03-31 | Cafeteria | Drinking Fountain in Cafeteria | Drinking Fountain | Initial | <5.00 | 2022-04-12
DW-01-GT-IN-CAFÉ-T2 | 24 | 2021-04-22 | Girls Cafeteria Restroom | Girls Cafeteria Restroom Right Tap | Faucet | Initial | <5.00 | 2021-06-15
DW-01-GT-IN-CAFÉ-T1 | 25 | 2021-04-22 | Girls Cafeteria Restroom | Girls Cafeteria Restroom Left Tap | Faucet | Initial | <5.00 | 2021-06-15
DW-02-WLR-IN-GYM-T | 52 | 2021-04-23 | Girls PE Office | Female Phys Ed Teacher Restroom Tap | Faucet | Initial | 7.52 | 2021-06-15
DW-01-GT-BY-111-T2 | 31 | 2021-04-22 | Girls Restroom by 111 | Girls Restroom By Room 111 Right Sink | Faucet | Initial | 5.64 | 2021-06-15
DW-01-GT-BY-111-T1 | 33 | 2021-04-22 | Girls Restroom by 111 | Girls Restroom By Room 111 Left Sink | Faucet | Initial | <5.00 | 2021-06-15
DW-02-GT-BY-203-T4 | 62 | 2021-04-23 | Girls Restroom Near 203 | Girls Restroom Near Room 203 Right Tap | Faucet | Initial | <5.00 | 2021-06-15
DW-02-GT-BY-203-T3 | 63 | 2021-04-23 | Girls Restroom Near 203 | Girls Restroom Near Room 203 Middle Right Tap | Faucet | Initial | <5.00 | 2021-06-15
DW-02-GT-BY-203-T2 | 64 | 2021-04-23 | Girls Restroom Near 203 | Girls Restroom Near Room 203 Middle Left Tap | Faucet | Initial | <5.00 | 2021-06-15
DW-02-GT-BY-203-T1 | 65 | 2021-04-23 | Girls Restroom Near 203 | Girls Restroom Near Room 203 Left Tap | Faucet | Initial | <5.00 | 2021-06-15
DW-02-RM-IN-GYM-B | 6 | 2022-02-23 | Gym | Gym North Bubbler | Bubbler | Initial | 35.7 | 2022-03-08
DW-01-HA-BY-104-BF | 25 | 2021-10-01 | Hall by 104 | Bottle Filler by Classroom 104 | Bottle Filler | Initial | <5.00 | 2021-10-08
DW-01-HA-BY-11S-DF | 1 | 2022-03-31 | Hall by 11S | Drinking Fountain in Hallway by 11S | Drinking Fountain | Initial | <5.00 | 2022-04-12
DW-01-HA-BY-121-B | 1 | 2021-10-01 | Hall by 121 | Bottle Filler Near Room 121 | Bottle Filler | Initial | <5.00 | 2021-10-08
DW-02-HA-BY-201-BF | 58 | 2021-04-23 | Hall by 201 | Bottle Filler Near Room 201 | Bottle Filler | Initial | <5.00 | 2021-06-15
DW-02-HA-BY-201-DF | 8 | 2022-03-31 | Hall by 201 | Drinking Fountain Near 201 | Drinking Fountain | Initial | <5.00 | 2022-04-12
DW-02-HA-BY-MLR-BF | 11 | 2021-10-01 | Hall by Boys PE Office | Bottle Filler Next to Male Phys Ed Teachers Locker Room | Bottle Filler | Initial | <5.00 | 2021-10-08
DW-01-HA-BY-FAC-DF | 4 | 2022-03-31 | Hall by Faculty Room | Drinking Fountain Near Faculty Room | Drinking Fountain | Initial | <5.00 | 2022-04-12
DW-02-HAN-BY-GYM-DF | 5 | 2022-03-31 | Hall by Gym | North Drinking Fountain near Gym | Drinking Fountain | Initial | <5.00 | 2022-04-12
DW-02-HAN-BY-GYM-BF | 6 | 2022-03-31 | Hall by Gym | North Bottle Filler Near Gym | Bottle Filler | Initial | <5.00 | 2022-04-12
DW-02-HAS-BY-GYM-DF | 7 | 2022-03-31 | Hall by Gym | South Drinking Fountain Near Gym | Drinking Fountain | Initial | <5.00 | 2022-04-12
DW-01-CR-IN-K1-T | 20 | 2021-04-22 | K1 | Classroom K1 Tap | Faucet | Initial | 6.37 | 2021-06-15
DW-01-BT-IN-K1-T | 21 | 2021-04-22 | K1 | Classroom K1 Bathroom Tap | Faucet | Initial | 6.56 | 2021-06-15
DW-01-CR-IN-K1-B | 3 | 2022-02-23 | K1 | Classroom K1 Bubbler | Bubbler | Initial | 14.5 | 2022-03-08
DW-01-CR-IN-K2-T | 22 | 2021-04-22 | K2 | Classroom K2 Tap | Faucet | Initial | 8.26 | 2021-06-15
DW-01-BT-IN-K2-T | 23 | 2021-04-22 | K2 | Classroom K2 Bathroom Tap | Faucet | Initial | 6.11 | 2021-06-15
DW-01-CR-IN-K2-B | 4 | 2022-02-23 | K2 | Classroom K2 Bubbler | Bubbler | Initial | 14.2 | 2022-03-08
DW-01-RM-IN-KI-T1 | 10 | 2021-04-22 | Kitchen | Cafeteria Kitchen Tap 1 (Working Clockwise) | Faucet | Initial | 11 | 2021-06-15
DW-01-RM-IN-KI-T2 | 11 | 2021-04-22 | Kitchen | Cafeteria Kitchen Tap 2 (Working Clockwise) | Faucet | Initial | <5.00 | 2021-06-15
DW-01-RM-IN-KI-T3 | 12 | 2021-04-22 | Kitchen | Cafeteria Kitchen Tap 3 (Working Clockwise) | Faucet | Initial | <5.00 | 2021-06-15
DW-01-RM-IN-SA-T | 13 | 2021-04-22 | Kitchen | Cafeteria Serving Area Tap | Faucet | Initial | 17.9 | 2021-06-15 | WO#149115. 6/23/2021 - Replaced fittings. 10 - 1/2" 90s pro press. 2 - 1/2" ball valves. 2 - 1/2" x 3/8" fittings. 2 - 1/2" x 3/8" x 12" braided supply lines.
DW-01-RM-IN-KI-T4 | 14 | 2021-04-22 | Kitchen | Cafeteria Kitchen Tap 4 (Working Clockwise) | Faucet | Initial | 22.4 | 2021-06-15 | WO#149116. 6/23/2021 - Flush and install new aerator.
DW-01-RM-IN-SA-T | 3 | 2021-10-01 | Kitchen | Cafeteria Serving Area Tap | Faucet | Post Remediation | 30.1 | 2021-10-08
DW-01-KSL-IN-T | 3 | 2022-03-31 | Kitchen | Cafeteria Serving Area Tap (Sink in Kitchen Serving Line) | Faucet | Post Remediation | 14.9 | 2022-04-12
DW-02-RM-IN-NO-T | 55 | 2021-04-23 | Nurse | Nurse's Office Tap | Faucet | Initial | <5.00 | 2021-06-15
DW-01-GT-BY-115-T | 6 | 2021-04-22 | Restroom by 115 - Left | Left Private (Near Room 115) Restroom Tap | Faucet | Initial | <5.00 | 2021-06-15
DW-01-BT-BY-115-T | 5 | 2021-04-22 | Restroom by 115 - Right | Right Private Restroom (Near Room 115) Tap | Faucet | Initial | <5.00 | 2021-06-15
DW-02-GT-BY-218-T | 44 | 2021-04-23 | Restroom by 118 - Left | Left Private (Near Room 118) Restroom Tap | Faucet | Initial | <5.00 | 2021-06-15
DW-02-BT-BY-218-T | 43 | 2021-04-23 | Restroom by 118 - Right | Right Private Restroom (Near Room 118) Tap | Faucet | Initial | <5.00 | 2021-06-15
DW-01-BT-BY-141-T | 15 | 2021-04-22 | Restroom by 141 | Bathroom Tap Near Room 141 | Faucet | Initial | <5.00 | 2021-06-15
DW-02-BT-BY-214-T | 56 | 2021-04-23 | Restroom by 214 | Restroom Near Room 214 Tap | Faucet | Initial | 14.8 | 2021-06-15
DW-02-BT-BY-NO-T | 57 | 2021-04-23 | Restroom by Nurse | Restroom Near Nurse's Office Tap | Faucet | Initial | 15.7 | 2021-06-15 | WO#149119 6/23/2021 - Flush and install new aerator.
DW-02-BT-BY-NO-T | 19 | 2021-10-01 | Restroom by Nurse | Restroom Near Nurse's Office Tap | Faucet | Post Remediation | 7.83 | 2021-10-08
DW-01-BT-IN-TL-T | 18 | 2021-04-22 | Teachers Lounge Restroom | Restroom In Teachers Lounge | Faucet | Initial | <5.00 | 2021-06-15

## Plank Rd North
Date Last Updated |  | 2023-01-12
School Name: |  | Plank Road North Elementary School
Lab ELAP ID# |  | NY63556 |  |  |  | Method of Analysis: |  |  | Metals 200.9
Lab ID# | School Sample ID # | Collection Date | Sample Location | Sample Location Description | Outlet Description | Initial/ Post Remediation | Lead Result mcg/L (ppb) | Lab Report Reciept Date | Action Taken for Outlets Greater than 15 mcg/L
PN-01-RM-IN-96-T | 44 | 2021-04-27 | 96 | Tap in Room 96 | Faucet | Initial | 27.7 | 2021-06-15 | WO#149122 - 7/31/21. Flushing. Replaced aerator.
PN-01-RM-IN-96-T | 23 | 2021-08-11 | 96 | Tap in Room 96 | Faucet | Post Remediation | 23.8 | 2021-08-23
PN-01-RM-IN-NO-T | 42 | 2021-04-27 | 97 | Nurse's Office Tap | Faucet | Initial | 8.11 | 2021-06-15
PN-01-CR-IN-100-T | 49 | 2021-04-27 | 100 | Classroom 100 Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-CR-IN-100-B | 19 | 2022-09-23 | 100 | Classroom 100 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
PN-01-CR-IN-101-T | 55 | 2021-04-27 | 101 | Classroom 101 Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-CR-IN-101-B | 22 | 2022-09-23 | 101 | Classroom 101 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
PN-01-CR-IN-102-T | 40 | 2021-04-27 | 102 | Classroom 102 Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-CR-IN-102-B | 12 | 2022-09-23 | 102 | Classroom 102 Bubbler | Bubbler | Initial | 6.61 | 2022-10-05
PN-01-CR-IN-103-T | 43 | 2021-04-27 | 103 | Classroom 103 Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-CR-IN-103-B | 13 | 2022-09-23 | 103 | Classroom 103 Bubbler | Bubbler | Initial | 6.68 | 2022-10-05
PN-01-CR-IN-104-T | 46 | 2021-04-27 | 104 | Classroom 104 Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-CR-IN-104-B | 14 | 2022-09-23 | 104 | Classroom 104 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
PN-01-CR-IN-105-T | 45 | 2021-04-27 | 105 | Classroom 105 Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-CR-IN-105-B | 15 | 2022-09-23 | 105 | Classroom 105 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
PN-01-CR-IN-106-T | 48 | 2021-04-27 | 106 | Classroom 106 Tap | Faucet | Initial | 8.27 | 2021-06-15
PN-01-CR-IN-106-B | 16 | 2022-09-23 | 106 | Classroom 106 Bubbler | Bubbler | Initial | 12.5 | 2022-10-05
PN-01-CR-IN-107-T | 47 | 2021-04-27 | 107 | Classroom 107 Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-CR-IN-107-B | 17 | 2022-09-23 | 107 | Classroom 107 Bubbler | Bubbler | Initial | 6.46 | 2022-10-05
PN-01-CR-IN-108-T | 50 | 2021-04-27 | 108 | Classroom 108 Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-CR-IN-108-B | 18 | 2022-09-23 | 108 | Classroom 108 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
PN-01-CR-IN-110-T | 56 | 2021-04-27 | 110 | Classroom 110 Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-CR-IN-110-B | 23 | 2022-09-23 | 110 | Classroom 110 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
PN-01-CR-IN-111-T | 63 | 2021-04-27 | 111 | Classroom 111 Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-CR-IN-111-B | 24 | 2022-09-23 | 111 | Classroom 111 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
PN-01-CR-IN-112-T | 64 | 2021-04-27 | 112 | Classroom 112 Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-CR-IN-112-B | 25 | 2022-09-23 | 112 | Classroom 112 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
PN-01-CR-IN-115-T | 67 | 2021-04-27 | 115 | Classroom 115 Tap | Faucet | Initial | 17.2 | 2021-06-15 | WO#149123 - 7/31/21. Replaced fittings. 1 - 1/2' male adaptor. 1 - 1/2" stop. 1 - chrome supply.
PN-01-CR-IN-115-T | 24 | 2021-08-11 | 115 | Classroom 115 Tap | Faucet | Post Remediation | 14 | 2021-08-23
PN-01-CR-IN-115-BF | 27 | 2022-09-23 | 115 | Classroom 115 Bottle Filler | Bottle Filler | Initial | 5.29 | 2022-10-05
PN-01-CR-IN-116-T | 68 | 2021-04-27 | 116 | Classroom 116 Tap | Faucet | Initial | 9.02 | 2021-06-15
PN-01-CR-IN-116-BF | 29 | 2022-09-23 | 116 | Classroom 116 Bottle Filler | Bottle Filler | Initial | <5.00 | 2022-10-05
PN-01-CR-IN-117-T | 66 | 2021-04-27 | 117 | Classroom 117 Tap | Faucet | Initial | 5.92 | 2021-06-15
PN-01-CR-IN-117-BF | 28 | 2022-09-23 | 117 | Classroom 117 Bottle Filler | Bottle Filler | Initial | <5.00 | 2022-10-05
PN-01-CR-IN-118-T | 65 | 2021-04-27 | 118 | Classroom 118 Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-CR-IN-118-BF | 26 | 2022-09-23 | 118 | Classroom 118 Bottle Filler | Bottle Filler | Initial | 10.7 | 2022-10-05
PN-01-BT-IN-121-T | 53 | 2021-04-27 | 121 | Restroom in Classroom 121 Tap | Faucet | Initial | 9.34 | 2021-06-15
PN-01-CR-IN-121-T | 54 | 2021-04-27 | 121 | Classroom 121 Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-CR-IN-121-B | 6 | 2022-02-24 | 121 | Classroom 121 Bubbler | Bubbler | Initial | 6.26 | 2022-03-08
PN-01-CR-IN-121-BF | 21 | 2022-09-23 | 121 | Classroom 121 Bottle Filler | Bottle Filler | Initial | 7.02 | 2022-10-05
PN-01-CR-IN-122-T | 51 | 2021-04-27 | 122 | Classroom 122 Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-BT-IN-122-T | 52 | 2021-04-27 | 122 | Restroom in Classroom 122 Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-CR-IN-122-B | 5 | 2022-02-24 | 122 | Classroom 122 Bubbler | Bubbler | Initial | <5.00 | 2022-03-08
PN-01-CR-IN-2-B | 11 | 2022-09-23 | 122 | Classroom 2 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
PN-01-CR-IN-122-BF | 20 | 2022-09-23 | 122 | Classroom 122 Bottle Filler | Bottle Filler | Initial | <5.00 | 2022-10-05
PN-01-RM-IN-KI-T3 | 28 | 2021-04-27 | 123 | Kitchen Right Tap (From Hall Outward Into Kitchen) | Faucet | Initial | <5.00 | 2021-06-15
PN-01-RM-IN-KI-T2 | 29 | 2021-04-27 | 123 | Kitchen Middle Tap (From Hall Outward Into Kitchen) | Faucet | Initial | <5.00 | 2021-06-15
PN-01-RM-IN-KI-T1 | 30 | 2021-04-27 | 123 | Kitchen Left Tap (From Hall Outward Into Kitchen) | Faucet | Initial | <5.00 | 2021-06-15
PN-01-RM-IN-LI-T | 25 | 2021-04-27 | 131 | Library Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-CR-IN-002-T | 26 | 2021-04-27 | 132 | Classroom 002 Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-RM-IN-001-T | 32 | 2021-04-27 | 133 | Room 001 Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-CR-IN-201-T | 24 | 2021-04-27 | 201 | Classroom 201 Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-CR-IN-201-B | 7 | 2022-09-23 | 201 | Classroom 201 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
PN-01-CR-IN-202-T | 23 | 2021-04-27 | 202 | Classroom 202 Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-CR-IN-202-B | 8 | 2022-09-23 | 202 | Classroom 202 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
PN-01-CR-IN-203-T | 22 | 2021-04-27 | 203 | Classroom 203 Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-CR-IN-203-B | 5 | 2022-09-23 | 203 | Classroom 203 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
PN-01-CR-IN-204-T | 21 | 2021-04-27 | 204 | Classroom 204 Tap | Faucet | Initial | 5.16 | 2021-06-15
PN-01-CR-IN-204-B | 6 | 2022-09-23 | 204 | Classroom 204 Bubbler | Bubbler | Initial | 12.5 | 2022-10-05
PN-01-CR-IN-205-T | 20 | 2021-04-27 | 205 | Classroom 205 Tap | Faucet | Initial | 5.37 | 2021-06-15
PN-01-CR-IN-205-B | 3 | 2022-09-23 | 205 | Classroom 205 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
PN-01-CR-IN-206-T | 19 | 2021-04-27 | 206 | Classroom 206 Tap | Faucet | Initial | 5.68 | 2021-06-15
PN-01-CR-IN-206-B | 4 | 2022-09-23 | 206 | Classroom 206 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
PN-01-CR-IN-207-T | 18 | 2021-04-27 | 207 | Classroom 207 Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-CR-IN-207-B | 2 | 2022-09-23 | 207 | Classroom 207 Bubbler | Bubbler | Initial | <5.00 | 2022-10-05
PN-01-CR-IN-208-T1 | 2 | 2021-04-27 | 208 | Room 208 Left Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-CR-IN-208-T2 | 3 | 2021-04-27 | 208 | Room 208 Middle Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-CR-IN-208-T3 | 4 | 2021-04-27 | 208 | Room 208 Right Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-CR-IN-208-B | 9 | 2022-09-23 | 208 | Classroom 208 Bubbler | Bubbler | Initial | 14 | 2022-10-05
PN-01-CR-IN-209-T | 8 | 2021-04-27 | 209 | Classroom 209 Tap | Faucet | Initial | 8.15 | 2021-06-15
PN-01-CR-IN-209-B | 10 | 2022-09-23 | 209 | Classroom 209 Bubbler | Bubbler | Initial | 8.03 | 2022-10-05
PN-01-CR-IN-210-T | 7 | 2021-04-27 | 210 | Classroom 210 Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-RM-IN COPY-T | 33 | 2021-04-27 | 122B | Copy Room Tap | Faucet | Initial | 19.3 | 2021-06-15 | WO#149120 - 7/31/21. Replaced fittings. 3 - 1/2" 90s, 1 - 1/2" 45, 1 - coupler, 1 - 1/2" ball valve, 1 - 1/2" x 3/8" compression, 1 - chrome supply.
PN-01-RM-IN COPY-T | 20 | 2021-08-11 | 122B | Copy Room Tap | Faucet | Post Remediation | <5.00 | 2021-08-23
PN-01-BT-IN-KI-T | 31 | 2021-04-27 | 123D | Kitchen Restroom Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-BT-IN-002-T | 27 | 2021-04-27 | 132 Restroom | Classroom 002 Restroom Tap | Faucet | Initial | 10.5 | 2021-06-15
PN-01-BT-IN-MO-T | 34 | 2021-04-27 | 134A | Main Office Restroom Tap | Faucet | Initial | 17.4 | 2021-06-15 | WO#149121 - 7/31/21. Flushing. Replaced aerator.
PN-01-BT-IN-MO-T | 22 | 2021-08-11 | 134A | Main Office Restroom Tap | Faucet | Post Remediation | 18 | 2021-08-23
PN-01-BLR-IN-GYM-T2 | 5 | 2021-04-27 | 212A | Boys Locker Room Right Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-BLR-IN-GYM-T1 | 6 | 2021-04-27 | 212A | Boys Locker Room Left Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-MLR-IN-GYM-T | 1 | 2021-04-27 | 213 Restroom | Male Phys Ed Teacher's Restroom Tap | Faucet | Initial | 8.81 | 2021-06-15
PN-01-WLR-IN-GYM-T | 9 | 2021-04-27 | 216 Restroom | Female Phys Ed Teacher's Restroom Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-GLR-IN-GYM-T1 | 16 | 2021-04-27 | 217A | Girls Locker Left Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-GLR-IN-GYM-T2 | 17 | 2021-04-27 | 217A | Girls Locker Right Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-BT-IN-NO-T | 41 | 2021-04-27 | 97C | Nurse's Office Restroom Tap | Faucet | Initial | 5.82 | 2021-06-15
PN-01-RM-IN-CAFÉ-BF | 21 | 2021-08-11 | Cafeteria | Cafeteria Bottle Filler | Bottle Filler | Initial | 7.71 | 2021-08-23
PN-01-HA-BY-CAFÉ-DF | 3 | 2022-04-01 | Cafeteria | Drinking Fountain by Cafeteria | Drinking Fountain | Initial | <5.00 | 2022-04-12
PN-01-RM-IN-GYM-BS | 1 | 2022-02-24 | Gym Boy's Side | Gym Southern Bubbler | Bubbler | Initial | 12.9 | 2022-03-08
PN-01-RM-IN-GYM-BN | 2 | 2022-02-24 | Gym Girl's Side | Gym Northern Bubbler | Bubbler | Initial | 19.6 | 2022-03-08
PN-01-RM-IN-GYM-BN | 1 | 2022-04-01 | Gym Girl's Side | Gym Northern Bubbler | Bubbler | Post Remediation | 15.1 | 2022-04-12
PN-01-GYM-IN-GPE-DF | 1 | 2022-09-23 | Gym Girl's Side | Girl's Gym Drinking Fountain | Bubbler | Post Remediation | <5.00 | 2022-10-05
PN-01-HA-BY-109-BF | 8 | 2022-02-24 | Hall b7 109 | Hallway by 109 Bottle Filler | Bottle Filler | Initial | <5.00 | 2022-03-08
PN-01-HA-BY-104-BF | 3 | 2022-02-24 | Hall by 104 | Hallway by 104 Drinking Fountain | Drinking Fountain | Initial | <5.00 | 2022-03-08
PN-01-HA-BY-104-DF | 4 | 2022-02-24 | Hall by 104 | Hallway by 104 Bottle Filler | Bottle Filler | Initial | <5.00 | 2022-03-08
PN-01-HA-BY-109-DF | 7 | 2022-02-24 | Hall by 109 | Hallway by 109 Drinking Fountain | Drinking Fountain | Initial | <5.00 | 2022-03-08
PN-01-HA-BY-205-DF | 2 | 2022-04-01 | Hall by 205 | Drinking Fountain by Room 205 | Drinking Fountain | Initial | <5.00 | 2022-04-12
PN-01-HA-BY-206-BF | 19 | 2021-08-11 | Hall by 206 | Bottle Filler by Room 206 | Bottle Filler | Initial | <5.00 | 2021-08-23
PN-01-CR-HA-BY-206-DF | 1 | 2022-12-28 | Hall by 206 | Drinking Fountain by Room 206 | Drinking Fountain | Initial | <1.00 | 2023-01-05
PN-01-HA-BY-206-BF | 2 | 2022-12-28 | Hall by 206 | Bottle Filler by Room 206 | Bottle Filler | Initial | <1.00 | 2023-01-05
PN-01-HA-BY-MO-BF | 35 | 2021-04-27 | Hall Near Main Office | Bottle Filler Near Main Office | Bottle Filler | Initial | <5.00 | 2021-06-15
PN-01-GT-BY-GYM-T3 | 13 | 2021-04-27 | T1 Restroom | Girls Restroom By Gym Right Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-GT-BY-GYM-T2 | 14 | 2021-04-27 | T1 Restroom | Girls Restroom By Gym Middle Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-GT-BY-GYM-T1 | 15 | 2021-04-27 | T1 Restroom | Girls Restroom By Gym Left Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-BT-BY-GYM-T1 | 10 | 2021-04-27 | T2 Restroom | Boys Restroom By Gym Left Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-BT-BY-GYM-T2 | 11 | 2021-04-27 | T2 Restroom | Boys Restroom By Gym Middle Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-BT-BY-GYM-T3 | 12 | 2021-04-27 | T2 Restroom | Boys Restroom By Gym Right Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-BT-BY-111-T1 | 57 | 2021-04-27 | T3 Restroom | Boys Restroom By Room 111 Left Sink | Faucet | Initial | <5.00 | 2021-06-15
PN-01-BT-BY-111-T2 | 59 | 2021-04-27 | T3 Restroom | Boys Restroom By Room 111 Middle Sink | Faucet | Initial | <5.00 | 2021-06-15
PN-01-BT-BY-111-T3 | 61 | 2021-04-27 | T3 Restroom | Boys Restroom By Room 111 Right Sink | Faucet | Initial | <5.00 | 2021-06-15
PN-01-GT-BY-111-T3 | 58 | 2021-04-27 | T4 Restroom | Girls Restroom By Room 111 Right Sink | Faucet | Initial | <5.00 | 2021-06-15
PN-01-GT-BY-111-T2 | 60 | 2021-04-27 | T4 Restroom | Girls Restroom By Room 111 Middle Sink | Faucet | Initial | <5.00 | 2021-06-15
PN-01-GT-BY-111-T1 | 62 | 2021-04-27 | T4 Restroom | Girls Restroom By Room 111 Left Sink | Faucet | Initial | <5.00 | 2021-06-15
PN-01-BT-BY-099-T2 | 36 | 2021-04-27 | T5 Restroom | Men's Restroom Near Room 099 Right Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-BT-BY-099-T1 | 37 | 2021-04-27 | T5 Restroom | Men's Restroom Near Room 099 Left Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-GT-BY-099-T2 | 38 | 2021-04-27 | T6 Restroom | Women's Restroom Near Room 099 Right Tap | Faucet | Initial | <5.00 | 2021-06-15
PN-01-GT-BY-099-T1 | 39 | 2021-04-27 | T6 Restroom | Women's Restroom Near Room 099 Left Tap | Faucet | Initial | <5.00 | 2021-06-15

## Willink
Date Last Updated |  | 2023-01-12
School Name: |  | Willink Middle School
Lab ELAP ID# |  | NY63556 |  |  |  | Method of Analysis: |  |  | Metals 200.9
Lab ID# | School Sample ID # | Collection Date | Sample Location | Sample Location Description | Outlet Description | Initial/ Post Remediation | Lead Result mcg/L (ppb) | Lab Report Reciept Date | Action Taken for Outlets Greater than 15 mcg/L
WMS-01-CR-IN-A105-T | 84 | 2021-04-29 | A105 | Tap In Classroom A105 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-CR-IN-A107-T | 82 | 2021-04-29 | A107 | Tap In Classroom A107 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-BT-BY-A111-T | 87 | 2021-04-29 | A108 | Men's Restroom Tap Near Classroom A111 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-GT-BY-A111-T | 86 | 2021-04-29 | A109 | Women's Restroom Tap Near Classroom A111 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-CR-IN-A110-T | 83 | 2021-04-29 | A110 | Tap In Classroom A110 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-CR-IN-A112-T | 81 | 2021-04-29 | A112 | Tap In Classroom A112 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-RM-IN-A116-T | 78 | 2021-04-29 | A116 | Nurse's Main Office Tap | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-OFC-IN-A116-T | 80 | 2021-04-29 | A117 | Nurse's Personal Office Tap | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-BT-IN-A116-T | 79 | 2021-04-29 | A119 | Nurse's Office Bathroom Tap | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-GT-BY-A121-T2 | 75 | 2021-04-29 | A124 | Girls Restroom Right Tap By Room A121 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-GT-BY-A121-T1 | 77 | 2021-04-29 | A124 | Girls Restroom Left Tap By Room A121 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-BT-BY-A121-T1 | 74 | 2021-04-29 | A125 | Boys Restroom Left Tap By Room A121 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-BT-BY-A121-T2 | 76 | 2021-04-29 | A125 | Boys Restroom Right Tap By Room A121 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-RM-IN-MO-T2 | 93 | 2021-04-29 | A130A | Main Office Tap | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-RM-IN-MO-T1 | 94 | 2021-04-29 | A131A | Principal's Office Tap | Faucet | Initial | <5.00 | 2021-06-15
WMS-02-GT-BY-A213-T2 | 89 | 2021-05-04 | A216 | Girls Restroom Right Tap By Room A213 | Faucet | Initial | <5.00 | 2021-06-15
WMS-02-GT-BY-A213-T1 | 91 | 2021-05-04 | A216 | Girls Restroom Left Tap By Room A213 | Faucet | Initial | <5.00 | 2021-06-15
WMS-02-BT-BY-A213-T1 | 88 | 2021-05-04 | A217 | Boys Restroom Left Tap By Room A213 | Faucet | Initial | <5.00 | 2021-06-15
WMS-02-BT-BY-A213-T2 | 90 | 2021-05-04 | A217 | Boys Restroom Right Tap By Room A213 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-CR-IN-B105-T | 65 | 2021-04-29 | B105 | Tap In Classroom B105 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-CR-IN-B107-T | 63 | 2021-04-29 | B107 | Tap In Classroom B107 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-BT-BY-B111-T | 68 | 2021-04-29 | B108 | Men's Restroom Tap Near Classroom B111 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-GT-BY-B111-T | 67 | 2021-04-29 | B109 | Women's Restroom Tap Near Classroom B111 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-CR-IN-B110-T | 64 | 2021-04-29 | B110 | Tap In Classroom B110 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-CR-IN-B112-T | 62 | 2021-04-29 | B112 | Tap In Classroom B112 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-RM-BY-B114-T | 61 | 2021-04-29 | B123 | Guidance Counselor Office Tap | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-GT-BY-B125-T2 | 58 | 2021-04-29 | B128 | Girls Restroom Right Tap By Room B125 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-GT-BY-B125-T1 | 60 | 2021-04-29 | B128 | Girls Restroom Left Tap By Room B125 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-BT-BY-B125-T1 | 57 | 2021-04-29 | B129 | Boys Restroom Left Tap By Room B125 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-BT-BY-B125-T2 | 59 | 2021-04-29 | B129 | Boys Restroom Right Tap By Room B125 | Faucet | Initial | <5.00 | 2021-06-15
WMS-02-GT-BY-B213-T2 | 70 | 2021-04-29 | B216 | Girls Restroom Right Tap By Room B213 | Faucet | Initial | <5.00 | 2021-06-15
WMS-02-GT-BY-B213-T1 | 72 | 2021-04-29 | B216 | Girls Restroom Left Tap By Room B213 | Faucet | Initial | <5.00 | 2021-06-15
WMS-02-BT-BY-B213-T1 | 69 | 2021-04-29 | B217 | Boys Restroom Left Tap By Room B213 | Faucet | Initial | <5.00 | 2021-06-15
WMS-02-BT-BY-B213-T2 | 71 | 2021-04-29 | B217 | Boys Restroom Right Tap By Room B213 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-CR-IN-C105-T | 48 | 2021-04-29 | C105 | Tap In Classroom C105 | Faucet | Initial | 8.72 | 2021-06-15
WMS-01-CR-IN-C107-T | 46 | 2021-04-29 | C107 | Tap In Classroom C107 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-BT-BY-C111-T | 51 | 2021-04-29 | C108 | Men's Restroom Tap Near Classroom C111 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-GT-BY-C111-T | 50 | 2021-04-29 | C109 | Women's Restroom Tap Near Classroom C111 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-CR-IN-C110-T | 47 | 2021-04-29 | C110 | Tap In Classroom C110 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-CR-IN-C112-T | 45 | 2021-04-29 | C112 | Tap In Classroom C112 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-GT-BY-C118-T2 | 41 | 2021-04-29 | C121 Restroom | Girls Restroom Right Tap By Room C118 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-GT-BY-C118-T1 | 43 | 2021-04-29 | C121 Restroom | Girls Restroom Left Tap By Room C118 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-BT-BY-C118-T1 | 40 | 2021-04-29 | C122 Restroom | Boys Restroom Left Tap By Room C118 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-BT-BY-C118-T2 | 42 | 2021-04-29 | C122 Restroom | Boys Restroom Right Tap By Room C118 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-RM-IN-C123-T | 44 | 2021-04-29 | C123 | Tap In Classroom C123 | Faucet | Initial | <5.00 | 2021-06-15
WMS-02-GT-BY-C213-T2 | 53 | 2021-04-29 | C216 | Girls Restroom Right Tap By Room C213 | Faucet | Initial | <5.00 | 2021-06-15
WMS-02-GT-BY-C213-T1 | 55 | 2021-04-29 | C216 | Girls Restroom Left Tap By Room C213 | Faucet | Initial | <5.00 | 2021-06-15
WMS-02-BT-BY-C213-T1 | 52 | 2021-04-29 | C217 | Boys Restroom Left Tap By Room C213 | Faucet | Initial | <5.00 | 2021-06-15
WMS-02-BT-BY-C213-T2 | 54 | 2021-04-29 | C217 | Boys Restroom Right Tap By Room C213 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-CR-IN-D103-T | 39 | 2021-04-29 | D103 | Classroom D103 Tap | Faucet | Initial | 13.1 | 2021-06-15
WMS-01-CR-IN-D103-B | 1 | 2022-12-28 | D103 | Classroom D103 Bubbler | Bubbler | Initial | 3 | 2023-01-05
WMS-01-CR-IN-D106-T | 36 | 2021-04-29 | D106 | Classroom D106 Tap | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-CR-IN-E103-T1 | 24 | 2021-04-29 | E103 | Classroom E103 Left Tap (Facing Wall) | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-CR-IN-E103-T2 | 25 | 2021-04-29 | E103 | Classroom E103 Right Tap (Facing Wall) | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-CR-IN-E105-T1 | 34 | 2021-04-29 | E105 | Classroom E105 Left Tap (Facing Wall) | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-CR-IN-E105-T2 | 35 | 2021-04-29 | E105 | Classroom E105 Right Tap (Facing Wall) | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-CR-IN-E106-T2 | 37 | 2021-04-29 | E106 | Classroom E106 Right Tap (Facing Wall) | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-CR-IN-E106-T1 | 38 | 2021-04-29 | E106 | Classroom E106 Left Tap (Facing Wall) | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-LIB-IN-T-T | 3 | 2022-12-28 | E110 | Library Private Restroom Tap | Faucet | Initial | 2 | 2023-01-05 | New fixture
WMS-01-BT-IN-LIB-T | 26 | 2021-04-29 | E113 | Library Private Restroom Tap | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-LIB-IN-RM-T | 2 | 2022-12-28 | E113 | Library Maker Space Tap | Faucet | Initial | <1.00 | 2023-01-05 | New fixture
WMS-01-BT-BY-LIB-T1 | 28 | 2021-04-29 | E113I | Men's Restroom Near Library Left Tap (Facing Wall) | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-BT-BY-LIB-T2 | 30 | 2021-04-29 | E113I | Men's Restroom Near Library Middle Tap (Facing Wall) | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-BT-BY-LIB-T3 | 32 | 2021-04-29 | E113I | Men's Restroom Near Library Right Tap (Facing Wall) | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-GT-BY-LIB-T3 | 27 | 2021-04-29 | E113J | Women's Restroom Near Library Right Tap (Facing Wall) | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-GT-BY-LIB-T2 | 29 | 2021-04-29 | E113J | Women's Restroom Near Library Middle Tap | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-GT-BY-LIB-T1 | 31 | 2021-04-29 | E113J | Women's Restroom Near Library Left Tap (Facing Wall) | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-RM-IN-BLR-T1 | 16 | 2021-04-29 | F105 | Boys Locker Room Left Tap | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-RM-IN-BLR-T2 | 17 | 2021-04-29 | F105 | Boys Locker Room Middle Tap | Faucet | Initial | 6.9 | 2021-06-15
WMS-01-RM-IN-BLR-T3 | 18 | 2021-04-29 | F105 | Boys Locker Room Right Tap | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-RM-BY-MLR-IM | 15 | 2021-04-29 | F106 | Ice Machine Near Male Phys Ed Teacher Locker Room | Ice Machine | Initial | <5.00 | 2021-06-15
WMS-01-RM-IN-GLR-T3 | 21 | 2021-04-29 | F111 | Girls Locker Room Right Tap | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-RM-IN-GLR-T2 | 22 | 2021-04-29 | F111 | Girls Locker Room Middle Tap | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-RM-IN-GLR-T1 | 23 | 2021-04-29 | F111 | Girls Locker Room Left Tap | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-RM-IN-WLR-T | 20 | 2021-04-29 | F112 | Female Phys Ed Teacher Locker Room Tap | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-CR-IN-G113-T | 12 | 2021-04-29 | G113 | Room G113 Tap | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-BT-IN-KLR-T | 11 | 2021-04-29 | G116 | Kitchen Locker Room Bathroom Tap | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-RM-IN-DWR-T1 | 9 | 2021-04-29 | G121A | Left Tap In Dishwashing Room | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-RM-IN-DWR-T2 | 10 | 2021-04-29 | G121A | Middle Tap in Dishwashing Room | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-RM-IN-KIT-T5 | 2 | 2021-04-29 | G122 | Kitchen Right Hand Sink Tap (On North Wall) | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-RM-IN-KIT-T2 | 3 | 2021-04-29 | G122 | Kitchen Middle Sink Tap (On North Wall) | Faucet | Initial | 8.83 | 2021-06-15
WMS-01-RM-IN-KIT-T3 | 4 | 2021-04-29 | G122 | Kitchen Northern Pot Filler | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-RM-IN-KIT-T4 | 5 | 2021-04-29 | G122 | Kitchen Southern Pot Filler | Faucet | Initial | 5.62 | 2021-06-15
WMS-01-RM-IN-KIT-T1 | 6 | 2021-04-29 | G122 | Kitchen Left Sink Tap (On North Wall) | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-RM-IN-KIT-CET | 7 | 2021-04-29 | G122 | Center Tap in Middle of Kitchen | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-RM-IN-KIT-CFT | 8 | 2021-04-29 | G122 | Coffee Tap Line in Kitchen | Coffee Tap | Initial | 23.3 | 2021-06-15 | WO#149124. 6/26/2021 - Replaced fittings. 1 - ball valve, 1 - 90. Installed new filter.
WMS-01-RM-IN-KIT-CFT | 14 | 2021-08-27 | G122 | Coffee Tap Line in Kitchen | Coffee Tap | Post Remediation | <5.00 | 2021-09-03
WMS-01-HA-BY-CAFÉ-BF | 1 | 2021-04-29 | Hall by Cafeteria | Bottle Filler Outside of Cafetorium | Bottle Filler | Initial | <5.00 | 2021-06-15
WMS-01-HA-BY-A111-BF | 85 | 2021-04-29 | Hall near A111 | Bottle Filler Near Classroom A111 | Bottle Filler | Initial | <5.00 | 2021-06-15
WMS-01-HA-BY-A111-DF | 5 | 2022-03-31 | Hall near A111 | Drinking Fountain by A111 | Drinking Fountain | Initial | <5.00 | 2022-04-12
WMS-01-HA-BY-A126-DF | 4 | 2022-03-31 | Hall near A126 | Drinking Fountain by A126 | Drinking Fountain | Initial | <5.00 | 2022-04-12
WMS-02-HA-BY-A207-BF | 92 | 2021-05-04 | Hall near A207 | Bottle Filler Near Classroom A207 | Bottle Filler | Initial | <5.00 | 2021-06-15
WMS-02-HA-BY-A207-DF | 6 | 2022-03-31 | Hall near A207 | Drinking Fountain by A207 | Drinking Fountain | Initial | <5.00 | 2022-04-12
WMS-01-HA-BY-B111-BF | 66 | 2021-04-29 | Hall near B111 | Bottle Filler Near Classroom B111 | Bottle Filler | Initial | <5.00 | 2021-06-15
WMS-01-HA-BY-B111-DF | 3 | 2022-03-31 | Hall near B111 | Drinking Fountain by B111 | Drinking Fountain | Initial | <5.00 | 2022-04-12
WMS-02-HA-BY-B207-BF | 73 | 2021-04-29 | Hall near B207 | Bottle Filler Near Classroom B207 | Bottle Filler | Initial | <5.00 | 2021-06-15
WMS-02-HA-BY-B207-DF | 7 | 2022-03-31 | Hall near B207 | Drinking Fountain by B207 | Drinking Fountain | Initial | <5.00 | 2022-04-12
WMS-01-HA-BY-C111-BF | 49 | 2021-04-29 | Hall near C111 | Bottle Filler Near Classroom C111 | Bottle Filler | Initial | <5.00 | 2021-06-15
WMS-01-HA-BY-C111-DF | 2 | 2022-03-31 | Hall near C111 | Drinking Fountain by C111 | Drinking Fountain | Initial | <5.00 | 2022-04-12
WMS-02-HA-BY-C207-BF | 56 | 2021-04-29 | Hall near C207 | Bottle Filler Near Classroom C207 | Bottle Filler | Initial | <5.00 | 2021-06-15
WMS-02-HA-BY-C207-DF | 8 | 2022-03-31 | Hall near C207 | Drinking Fountain by C207 | Drinking Fountain | Initial | <5.00 | 2022-04-12
WMS-01-HA-BY-CAFÉ-DF | 1 | 2022-03-31 | Hall near Cafeteria | Drinking Fountain by Cafeteria | Drinking Fountain | Initial | <5.00 | 2022-04-12
WMS-01-HA-BY-WR-BF | 19 | 2021-04-29 | Hall near F108 | Bottle Filler Near Weight Room | Bottle Filler | Initial | <5.00 | 2021-06-15
WMS-01-HA-BY-WR-DF | 9 | 2022-03-31 | Hall near F108 | Drinking Fountain by Weight Room | Drinking Fountain | Initial | <5.00 | 2022-04-12
WMS-01-HA-BY-KIT-DF | 1 | 2022-02-23 | Hall near Kitchen | Drinking Fountain Outside of Kitchen | Drinking Fountain | Initial | <5.00 | 2022-03-08
WMS-01-HA-BY-LIB-BF | 33 | 2021-04-29 | Hall North Side of Library | Bottle Filler Near Library (North of Library) | Bottle Filler | Initial | <5.00 | 2021-06-15
WMS-01-BT-BY-G105-T | 13 | 2021-04-29 | Men's Room Across From G109 | Men's Restroom Tap Near Room G105 | Faucet | Initial | <5.00 | 2021-06-15
WMS-01-GT-BY-G105-T | 14 | 2021-04-29 | Women's Room Across From G109 | Women's Restroom Tap Near Room G105 | Faucet | Initial | <5.00 | 2021-06-15

## Spry
Date Last Updated |  | 2023-01-12
School Name: |  | Spry Middle School
Lab ELAP ID# |  | NY63556 |  |  |  | Method of Analysis: |  |  | Metals 200.9
Lab ID# | School Sample ID # | Collection Date | Sample Location | Sample Location Description | Outlet Description | Initial/ Post Remediation | Lead Result mcg/L (ppb) | Lab Report Reciept Date | Action Taken for Outlets Greater than 15 mcg/L
SMS-01-RM-IN-REC-T | 49 | 2021-05-06 | 98 | Tap in Current Receiving Room | Faucet | Initial | <5.00 | 2021-06-15
SMS-01-RM-IN-LIB-T | 45 | 2021-05-06 | 103 | Tap in Library | Faucet | Initial | <5.00 | 2021-06-15
SP-01-LR-IN-GLR-DF | 1 | 2022-12-28 | 106 | Girls Locker Room Drinking Fountain | Drinking Fountain | Initial | <1.00 | 2023-01-05
SMS-01-RM-IN-NO-T | 42 | 2021-05-06 | 108 | Tap In Nurse's Main Office | Faucet | Initial | <5.00 | 2021-06-15
SMS-01-RM-IN-SEC-T | 39 | 2021-05-06 | 113 | Tap In Security Office | Faucet | Initial | <5.00 | 2021-06-15
SMS-01-BT-IN-SEC-T | 40 | 2021-05-06 | 113 | Tap In Security Office Bathroom | Faucet | Initial | <5.00 | 2021-06-15
SMS-01-RM-IN-121-T | 1 | 2021-05-05 | 121 | Tap in Room 121 | Faucet | Initial | <5.00 | 2021-06-15
SMS-01-CR-IN-129-T3 | 2 | 2021-05-05 | 129 | Classroom 129 Right Tap | Faucet | Initial | <5.00 | 2021-06-15
SMS-01-CR-IN-129-T2 | 4 | 2021-05-05 | 129 | Classroom 129 Center Tap | Faucet | Initial | <5.00 | 2021-06-15
SMS-01-CR-IN-129-T1 | 6 | 2021-05-05 | 129 | Classroom 129 Left Tap | Faucet | Initial | <5.00 | 2021-06-15
SMS-01-CR-IN-131-T1 | 3 | 2021-05-05 | 131 | Classroom 131 Left Tap | Faucet | Initial | 5.38 | 2021-06-15
SMS-01-CR-IN-131-T2 | 5 | 2021-05-05 | 131 | Classroom 131 Center Tap | Faucet | Initial | <5.00 | 2021-06-15
SMS-01-CR-IN-131-T3 | 7 | 2021-05-05 | 131 | Classroom 131 Right Tap | Faucet | Initial | <5.00 | 2021-06-15
SMS-01-CR-IN-132-T | 19 | 2021-05-05 | 132 | Classroom 132 Tap | Faucet | Initial | <5.00 | 2021-06-15
SMS-01-CR-IN-134-T | 20 | 2021-05-05 | 134 | Classroom 134 Tap | Faucet | Initial | <5.00 | 2021-06-15
SMS-01-CR-IN-140-T | 22 | 2021-05-05 | 140 | Classroom 140 Tap | Faucet | Initial | <5.00 | 2021-06-15
SMS-02-CR-IN-208-T | 51 | 2021-05-06 | 208 | Classroom 208 Tap | Faucet | Initial | <5.00 | 2021-06-15
SMS-02-RM-BY-215-T | 50 | 2021-05-06 | 210 | Tap In District Training Center (Near Room 215) | Faucet | Initial | <5.00 | 2021-06-15
SMS-02-RM-IN-217-T | 35 | 2021-05-06 | 217 | Tap In Room 217 | Faucet | Initial | 12 | 2021-06-15
SMS-02-CR-IN-232-T | 23 | 2021-05-06 | 232 | Classroom 232 Tap | Faucet | Initial | 6.14 | 2021-06-15
SMS-02-CR-IN-234-T | 24 | 2021-05-06 | 234 | Classroom 234 Tap | Faucet | Initial | <5.00 | 2021-06-15
SMS-02-RM-BY-CAFÉ-T | 25 | 2021-05-05 | 235 | Cafeteria Second Floor Break Room Tap | Faucet | Initial | <5.00 | 2021-06-15
SMS-02-CR-IN-236-T | 26 | 2021-05-05 | 236 | Classroom 236 Tap | Faucet | Initial | <5.00 | 2021-06-15
SMS-02-CR-IN-244-T | 27 | 2021-05-05 | 244 | Classroom 244 Tap | Faucet | Initial | <5.00 | 2021-06-15
SMS-03-GT-IN-ADMIN-T4 | 53 | 2021-05-06 | 316 | Women's Administration Restroom Right Tap | Faucet | Initial | 22.4 | 2021-06-15 | WO#149126. Handwashing sink only. 8/3/2021 - New aerator installed.
SMS-03-GT-IN-ADMIN-T3 | 54 | 2021-05-06 | 316 | Women's Administration Restroom Right Middle Tap | Faucet | Initial | <5.00 | 2021-06-15
SMS-03-GT-IN-ADMIN-T2 | 55 | 2021-05-06 | 316 | Women's Administration Restroom Left Middle Tap | Faucet | Initial | <5.00 | 2021-06-15
SMS-03-GT-IN-ADMIN-T1 | 56 | 2021-05-06 | 316 | Women's Administration Restroom Left Tap | Faucet | Initial | <5.00 | 2021-06-15
SP-03-WT-IN-WA-T4 | 10 | 2022-04-01 | 316 | 4th Sink in Admin Women's Room (Women's Administration Restroom Right Tap) | Faucet | Post Remediation | <5.00 | 2022-04-12
SMS-03-BT-IN-ADMIN-T2 | 57 | 2021-05-06 | 317 | Men's Adminstration Restroom Right Tap | Faucet | Initial | <5.00 | 2021-06-15
SMS-03-BT-IN-ADMIN-T1 | 58 | 2021-05-06 | 317 | Men's Adminstration Restroom Left Tap | Faucet | Initial | <5.00 | 2021-06-15
SMS-03-RM-IN-ADMINKIT-T | 59 | 2021-05-06 | 318 | Tap In Administration Kitchen | Faucet | Initial | <5.00 | 2021-06-15
SMS-03-CR-IN-326-T1 | 30 | 2021-05-06 | 326 | Classroom 326 Tap #1 | Faucet | Initial | <5.00 | 2021-06-15
SMS-03-CR-IN-326-T2 | 31 | 2021-05-06 | 326 | Classroom 326 Tap #2 | Faucet | Initial | 5.1 | 2021-06-15
SMS-03-CR-IN-326-T3 | 32 | 2021-05-06 | 326 | Classroom 326 Tap #3 | Faucet | Initial | <5.00 | 2021-06-15
SMS-03-CR-IN-326-T4 | 33 | 2021-05-06 | 326 | Classroom 326 Tap #4 | Faucet | Initial | 20.7 | 2021-06-15 | WO#149125. 8/3/2021. Installed new faucet, Replace fittings - 1 - 1/2" 90, 1 - 1/2" stop, 1 - supply line.
SMS-03-CR-IN-326-T5 | 34 | 2021-05-06 | 326 | Classroom 326 Tap #5 | Faucet | Initial | <5.00 | 2021-06-15
SMS-03-CR-IN-326-T4 | 22 | 2021-08-27 | 326 | Classroom 326 Tap #4 | Faucet | Post Remediation | <5.00 | 2021-09-03
SMS-01-BT-IN-MLR-IM | 48 | 2021-05-06 | 101A | Male Coach's Locker Room Ice Machine | Ice Maker | Initial | <5.00 | 2021-06-15
SMS-01-BT-IN-MLR-T | 47 | 2021-05-06 | 101A Restroom | Male Coach's Locker Room Bathroom Tap | Faucet | Initial | <5.00 | 2021-06-15
SMS-01-GT-IN-WLR-T | 44 | 2021-05-06 | 106A Restroom | Female Coach's Locker Room Bathroom Tap | Faucet | Initial | <5.00 | 2021-06-15
SMS-01-BT-IN-NO-T | 43 | 2021-05-06 | 108B | Bathroom Tap In Nurse's Office | Faucet | Initial | <5.00 | 2021-06-15
SMS-01-RM-BY-REC-T | 41 | 2021-05-06 | 112A | Tap in Old Receiving Room | Faucet | Initial | <5.00 | 2021-06-15
SMS-01-BT-IN-KSR-T | 8 | 2021-05-05 | 133 Restroom | Kitchen Storage Room Restroom Tap | Faucet | Initial | <5.00 | 2021-06-15
SMS-01-RM-IN-KIT-T1 | 9 | 2021-05-05 | 135A | Kitchen Tap #1 | Faucet | Initial | <5.00 | 2021-06-15
SMS-01-RM-IN-KIT-T2 | 11 | 2021-05-05 | 135A | Kitchen Tap #2 | Faucet | Initial | <5.00 | 2021-06-15
SMS-01-RM-IN-KIT-T3 | 12 | 2021-05-05 | 135A | Kitchen Tap #3 | Faucet | Initial | <5.00 | 2021-06-15
SMS-01-RM-IN-KIT-CT | 13 | 2021-05-05 | 135A | Large Pot Cooking Tap | Pot Filler | Initial | <5.00 | 2021-06-15
SMS-01-RM-IN-KIT-T4 | 14 | 2021-05-05 | 135A | Kitchen Tap #4 | Faucet | Initial | 6.2 | 2021-06-15
SMS-01-RM-IN-KIT-T5 | 15 | 2021-05-05 | 135A | Kitchen Tap #5 | Faucet | Initial | <5.00 | 2021-06-15
SMS-01-RM-IN-KIT-IM | 16 | 2021-05-05 | 135A | Kitchen Ice Machine | Ice Maker | Initial | <5.00 | 2021-06-15
SMS-01-RM-IN-KIT-T6 | 17 | 2021-05-05 | 135A | Kitchen Tap #6 (Next to Ice Machine) | Faucet | Initial | <5.00 | 2021-06-15
SMS-01-RM-IN-SRV-T1 | 10 | 2021-05-05 | 135B | Serving Area Tap #1 (Northern Tap) | Faucet | Initial | <5.00 | 2021-06-15
SMS-01-RM-IN-SRV-T2 | 18 | 2021-05-05 | 135B | Serving Area Tap #2 (Southern Tap) | Faucet | Initial | <5.00 | 2021-06-15
SMS-03-RM-IN-CRW-T | 29 | 2021-05-06 | 309H | Western Curriculum Room (Administration Wing) Tap | Faucet | Initial | <5.00 | 2021-06-15
SP-02-HA-BY-236-DF | 2 | 2022-04-01 | Hall by 236 | Drinking Fountain by 236 | Drinking Fountain | Initial | <5.00 | 2022-04-12
SMS-01-HA-BY-106-DF | 5 | 2022-02-25 | Hall by 106 | Drinking Fountain Near 106 | Drinking Fountain | Initial | <5.00 | 2022-03-08
SP-01-HA-BY-AO-DF | 3 | 2022-04-01 | Hall by 113 | Drinking Fountain by Attendance Office | Drinking Fountain | Initial | <5.00 | 2022-04-12
SMS-01-HA-BY-123-DF | 1 | 2022-02-24 | Hall by 123 | Drinking Fountain Near Classroom 123 | Drinking Fountain | Initial | <5.00 | 2022-03-08
SMS-01-HA-BY-125-DF | 2 | 2022-02-24 | Hall by 125 | Drinking Fountain Near Classroom 125 | Drinking Fountain | Initial | <5.00 | 2022-03-08
SMS-02-HA-BY-201-DF | 4 | 2022-02-25 | Hall by 201 | Drinking Fountain Near Room 201 | Drinking Fountain | Initial | <5.00 | 2022-03-08
SMS-02-HA-BY-224-DF | 3 | 2022-02-24 | Hall by 224 | Drinking Fountain Near Classroom 224 | Drinking Fountain | Initial | <5.00 | 2022-03-08
SMS-02-HA-BY-225-DF | 4 | 2022-02-24 | Hall by 225 | Drinking Fountain Near Classroom 225 | Drinking Fountain | Initial | <5.00 | 2022-03-08
SMS-03-HA-BY-324-DF | 5 | 2022-02-24 | Hall by 324 | Drinking Fountain Near Classroom 324 | Drinking Fountain | Initial | <5.00 | 2022-03-08
SMS-03-HA-BY-325-DF | 6 | 2022-02-24 | Hall by 325 | Drinking Fountain Near Classroom 325 | Drinking Fountain | Initial | <5.00 | 2022-03-08
SP-01-HA-BY-C2B-DF | 1 | 2022-04-01 | Hall by C2B | Drinking Fountain by C2B | Drinking Fountain | Initial | <5.00 | 2022-04-12
SP-01-HA-BY-GYM-DF | 4 | 2022-04-01 | Hall by Gym | Drinking Fountain by Gym | Drinking Fountain | Initial | <5.00 | 2022-04-12
SMS-02-HA-BY-SPDT-BF | 52 | 2021-05-06 | Hall by Superintedent Office | Bottle Filler Near Superintendent's | Bottle Filler | Initial | <5.00 | 2021-06-15
SMS-03-HA-BY-W33-DF | 3 | 2022-02-25 | Hall by Superintedent Office | Drinking Fountain Near Superintendent's Office | Drinking Fountain | Initial | <5.00 | 2022-03-08
SMS-01-HA-BY-W13-DF | 1 | 2022-02-25 | Hall by W13 | Drinking Fountain Near Classroom W13 | Drinking Fountain | Initial | 9.35 | 2022-03-08
SMS-02-HA-BY-W23-DF | 2 | 2022-02-25 | Hall by W23 | Drinking Fountain Near Classroom W23 | Drinking Fountain | Initial | <5.00 | 2022-03-08
SMS-01-HA-BY-102-BF | 46 | 2021-05-06 | Hall near 102 | Bottle Filler Near Room 102 | Bottle Filler | Initial | <5.00 | 2021-06-15
SMS-01-HA-BY-SEC-BF | 38 | 2021-05-06 | Hall Near 113 | Bottle Filler Outside of Security Office | Bottle Filler | Initial | <5.00 | 2021-06-15
SMS-01-HA-BY-138-BF | 21 | 2021-05-05 | Hall near 138 | Bottle Filler Near Room 138 | Bottle Filler | Initial | <5.00 | 2021-06-15
SP-02-HA-BY-210-DF | 5 | 2022-04-01 | Hall near 210 | Drinking Fountain by 210 | Drinking Fountain | Initial | <5.00 | 2022-04-12
SMS-02-HA-BY-217-BF | 36 | 2021-05-06 | Hall near 217 | Bottle Filler Near Room 217 | Bottle Filler | Initial | <5.00 | 2021-06-15
SP-02-HA-BY-304-DF | 11 | 2022-04-01 | Hall near 301 | Drinking Fountain by 301 | Drinking Fountain | Initial | <5.00 | 2022-04-12
SP-03-HA-BY-310-DF | 8 | 2022-04-01 | Hall near 310 | Drinking Fountain by 310 | Drinking Fountain | Initial | <5.00 | 2022-04-12
SP-03-HA-BY-311A-DF | 9 | 2022-04-01 | Hall near 311A | Drinking Fountain by 311A | Drinking Fountain | Initial | <5.00 | 2022-04-12
SMS-03-HA-BY-ELEV-BF | 37 | 2021-05-06 | Hall near Admin Elevator 3rd Floor | Bottle Filler Near Administration Elevator (3rd Floor) | Bottle Filler | Initial | <5.00 | 2021-06-15
SP-02-HA-BY-W23-DF | 6 | 2022-04-01 | Hall near W23 | Drinking Fountain by W23 | Drinking Fountain | Initial | <5.00 | 2022-04-12
SP-02-HA-BY-W23-BF | 7 | 2022-04-01 | Hall near W3 | Bottle Filler by W23 | Bottle Filler | Initial | <5.00 | 2022-04-12
SMS-02-BT-BY-243-T | 28 | 2021-05-05 | T1 | Restroom Tap by Classroom 243 | Faucet | Initial | <5.00 | 2021-06-15

## Schroeder
Date Last Updated |  | 2023-01-12
School Name: |  | Schroeder High School
Lab ELAP ID# |  | NY63556 |  |  |  | Method of Analysis: |  |  | Metals 200.9
Lab ID# | School Sample ID # | Collection Date | Sample Location | Sample Location Description | Outlet Description | Initial/ Post Remediation | Lead Result mcg/L (ppb) | Lab Report Reciept Date | Action Taken for Outlets Greater than 15 mcg/L
SGH-01-RM-IN-RM-T1 | 79 | 2021-05-11 | Greenhouse | Tap 1 in Greenhouse, Closest to Entrance | Faucet | Initial | 7.19 | 2021-06-15
SGH-01-RM-IN-RM-IM | 80 | 2021-05-11 | Greenhouse | Ice Machine in Greenhouse | Ice Maker | Initial | <5.00 | 2021-06-15
SGH-01-RM-IN-RM-T2 | 81 | 2021-05-11 | Greenhouse | Tap 2 in Greenhouse, Next Closest to Entrance | Faucet | Initial | <5.00 | 2021-06-15
SGH-01-RM-IN-RM-T3 | 82 | 2021-05-11 | Greenhouse | Tap 3 in Greenhouse, Furthest From Entrance | Faucet | Initial | <5.00 | 2021-06-15
SHS-02-HA-BY-W201-BF | 73 | 2021-05-11 | Hall by W202 | Bottle Filler Near Room W202 | Bottle Filler | Initial | <5.00 | 2021-06-15
SHS-02-HA-BY-W212-BF | 65 | 2021-05-11 | Hall by W212 | Bottle Filler Near Classroom W212 | Bottle Filler | Initial | <5.00 | 2021-06-15
SHS-01-HA-BY-W3-BF | 72 | 2021-05-11 | Hall by W3 | Bottle Filler Near Room W3 | Bottle Filler | Initial | <5.00 | 2021-06-15
SHS-01-CR-IN-NW3-T2 | 67 | 2021-05-11 | NW3 | Right Tap In Classroom NW3 | Faucet | Initial | <5.00 | 2021-06-15
SHS-01-CR-IN-NW3-T1 | 68 | 2021-05-11 | NW3 | Left Tap In Classroom NW3 | Faucet | Initial | <5.00 | 2021-06-15
SHS-01-CR-IN-NW5-T1 | 69 | 2021-05-11 | NW5 | Left Tap In Classroom NW5 | Faucet | Initial | <5.00 | 2021-06-15
SHS-01-CR-IN-NW5-T2 | 70 | 2021-05-11 | NW5 | Right Tap In Classroom NW5 | Faucet | Initial | <5.00 | 2021-06-15
SHS-01-RM-BY-TSL-T | 26 | 2021-05-11 | S2A | Tap Next to Door Leading to Teacher's Café Serving Line | Faucet | Initial | 184 | 2021-06-15 | WO#149132 - 8/21/21. Labeled "Non-Potable Water. Not for Drinking or Cooking Use"
SHS-01-RM-IN-TSL-T | 27 | 2021-05-11 | S2A | Tap In Teacher's Café Room Serving Line | Faucet | Initial | 53.2 | 2021-06-15 | WO#149133 - 8/21/21. Labeled "Non-Potable Water. Not for Drinking or Cooking Use"
SHS-01-RM-BY-EFPREP-TS | 28 | 2021-05-11 | S8 | Southern Tap Eastern Kitchen Food Prep Area | Faucet | Initial | 18 | 2021-06-15 | WO#149134. 8/21/21 - Relaced fittings. 2 - 3/8" hoses supply, 1 - new faucet, 2 - 1/2" brass stops, 2 - 1/2" x 3/4" 90s.
SHS-01-RM-BY-EFPREP-TN | 29 | 2021-05-11 | S8 | Northern Tap Eastern Kitchen Food Prep Area | Faucet | Initial | 60 | 2021-06-15 | WO#149135. 8/21/21. Replaced faucet.
SHS-02-RM-BY-KIMS-T | 30 | 2021-05-11 | S8 | Tap Next to Eastern Kitchen Meat Slicer | Faucet | Initial | 13.6 | 2021-06-15
SHS-01-RM-IN-WKI-T1 | 47 | 2021-05-11 | S8 | Western Kitchen Tap 1 | Faucet | Initial | <5.00 | 2021-06-15
SHS-01-RM-IN-WKI-T2 | 48 | 2021-05-11 | S8 | Western Kitchen Tap 2 | Faucet | Initial | 6.81 | 2021-06-15
SHS-01-RM-IN-WKI-T3 | 49 | 2021-05-11 | S8 | Western Kitchen Tap 3 | Faucet | Initial | 6.06 | 2021-06-15
SHS-01-RM-IN-WKI-T4 | 50 | 2021-05-11 | S8 | Western Kitchen Tap 4 | Faucet | Initial | 6.39 | 2021-06-15
SHS-01-RM-IN-WKI-PF1 | 51 | 2021-05-11 | S8 | Western Kitchen Potfiller 1 | Pot Filler | Initial | <5.00 | 2021-06-15
SHS-01-RM-IN-WKI-PF2 | 52 | 2021-05-11 | S8 | Western Kitchen Potfiller 2 | Pot Filler | Initial | <5.00 | 2021-06-15
SHS-01-RM-IN-WKI-T5 | 53 | 2021-05-11 | S8 | Western Kitchen Tap 5 (near serving area) | Faucet | Initial | 21.2 | 2021-06-15 | WO#149139. 8/21/21 - Labeled "Non-Potable Water. Not for Drinking or Cooking Use"
SHS-01-RM-IN-WKI-T6 | 54 | 2021-05-11 | S8 | Western Kitchen Tap 6 (near serving area) | Faucet | Initial | 11.1 | 2021-06-15
SHS-01-RM-IN-ESL-T1 | 31 | 2021-05-11 | S8A | Eastern Serving Line Left Tap (As you face wall with sinks) | Faucet | Initial | 13.1 | 2021-06-15
SHS-01-RM-IN-ESL-T2 | 32 | 2021-05-11 | S8A | Eastern Serving Line Right (As you face wall with sinks) | Faucet | Initial | 6.43 | 2021-06-15
SHS-01-CR-IN-SW3-T | 61 | 2021-05-11 | SW3 | Tap In Classroom SW3 | Faucet | Initial | 11.4 | 2021-06-15
SHS-01-CR-IN-SW6-T | 62 | 2021-05-11 | SW6 | Tap In Classroom SW6 | Faucet | Initial | 6.12 | 2021-06-15
STF-01-RM-IN-CONC-T | 76 | 2021-05-11 | Turf Field Concession | Turf Field Concessions Stand Tap | Faucet | Initial | 9.4 | 2021-06-15
STF-01-RM-IN-CONC-HCT | 77 | 2021-05-11 | Turf Field Concession | Turf Field Concessions Stand Hot Chocolate Tap | Hot Chocolate Tap | Initial | 27.1 | 2021-06-15 | WO#149141. 8/14/21 - Replaced fittings. 1 - 1/2" ball valve, 1 - 1/2" male adapter.
STF-01-RM-IN-CONC-CT | 78 | 2021-05-11 | Turf Field Concession | Turf Field Concessions Stand Coffee Tap | Coffee Tap | Initial | 16 | 2021-06-15 | WO#149142. 8/14/21 - Replaced fittings. 1 - 1/2" gate valve, 1 - 1/2" male adapter, 1 - 1/2" ball valve.
SHS-01-RM-IN-W11-T | 66 | 2021-05-11 | W11 | Tap In Room W11 | Faucet | Initial | 9.76 | 2021-06-15
SHS-01-RM-IN-W2-T | 74 | 2021-05-11 | W2 | Tap In Room W2 | Faucet | Initial | 8.58 | 2021-06-15
SHS-02-CR-IN-W201-T | 75 | 2021-05-11 | W201 | Tap In Classroom W201 | Faucet | Initial | 156 | 2021-06-15 | WO#149140. 8/14/21 - Replaced fittings. 1 - 1/2"brass valve, 1 - chrome supply, 2 - 1/2" 90s, 1 - 3/8" x 1/2" brass compression.
SHS-02-CR-IN-W212-T | 64 | 2021-05-11 | W212 | Tap In Classroom W212 | Faucet | Initial | 12.1 | 2021-06-15
SHS-02-CR-IN-W221-T | 63 | 2021-05-11 | W221 | Tap in Classroom W221 | Faucet | Initial | 7.82 | 2021-06-15
SHS-02-CR-IN-W228-T | 58 | 2021-05-11 | W228 | Tap in Room W228 | Faucet | Initial | 11.5 | 2021-06-15
SHS-01-CR-IN-W22-T | 60 | 2021-05-11 | W228 | Tap In Classroom W22 | Faucet | Initial | 8.76 | 2021-06-15
SHS-01-RM-IN-W28-T | 56 | 2021-05-11 | W28 | Tap In Room W28 | Faucet | Initial | 10.3 | 2021-06-15
SHS-01-RM-IN-W28-CT | 57 | 2021-05-11 | W28 | Coffee Tap In Room W28 | Coffee Tap | Initial | <5.00 | 2021-06-15
SHS-01-HA-BY-W28-BF | 59 | 2021-05-11 | W28 | Bottle Filler Near W28 | Bottle Filler | Initial | <5.00 | 2021-06-15
SHS-01-RM-IN-W7-T | 71 | 2021-05-11 | W7 | Tap In Room W7 | Faucet | Initial | <5.00 | 2021-06-15
SHS-01-CR-IN-E10-T3 | 14 | 2021-05-12 | E10 | Right Tap In Classroom E10 | Faucet | Initial | <5.00 | 2021-06-15
SHS-01-CR-IN-E10-T2 | 15 | 2021-05-12 | E10 | Middle Tap In Classroom E10 | Faucet | Initial | <5.00 | 2021-06-15
SHS-01-CR-IN-E10-T1 | 16 | 2021-05-12 | E10 | Left Tap In Classroom E10 | Faucet | Initial | <5.00 | 2021-06-15
SHS-01-CR-IN-E12-T | 11 | 2021-05-12 | E12 | Left Tap In Classroom E12 | Faucet | Initial | <5.00 | 2021-06-15
SHS-01-CR-IN-E12-T2 | 12 | 2021-05-12 | E12 | Middle Tap In Classroom E12 | Faucet | Initial | <5.00 | 2021-06-15
SHS-01-CR-IN-E12-T3 | 13 | 2021-05-12 | E12 | Right Tap In Classroom E12 | Faucet | Initial | <5.00 | 2021-06-15
SHS-02-RM-IN-LAC-T | 8 | 2021-05-12 | E13 | Lactation Room Tap | Faucet | Initial | 39.8 | 2021-06-15 | WO#149127 - 8/7/2021. Replaced fittings. 4 - 1/2" 90s, 1 - 1/2" gates valve, 1 - 1/2" chrome stop, 1 - 1/2" Brass 90.
SHS-01-CR-IN-E14-T | 10 | 2021-05-12 | E14 | Tap In Classroom E14 | Faucet | Initial | 35 | 2021-06-15 | WO#149129 - 8/7/21. Flush and replace aerator.
SHS-01-CR-IN-E16-T | 9 | 2021-05-12 | E16 | Tap In Classroom E16 | Faucet | Initial | 15.6 | 2021-06-15 | WO#149128 - 8/7/2021. Replaced fittings. 2 - 1/2" 90s, 1 - Ball Valve 1/2", 2 - male adapter 1/2", 1 - 1/2" x 3/8" compression.
SHS-02-RM-IN-E2-T | 33 | 2021-05-12 | E2 | Tap in Room E2 | Faucet | Initial | 6.67 | 2021-06-15
SHS-01-RM-IN-E202-T | 24 | 2021-05-12 | E202 | Tap In Room E202 | Faucet | Initial | 46.6 | 2021-06-15 | WO#149130 - 8/7/2021. Replaced fittings. 1 - 1/2" gate valve, 1 - 1/2" brass stop, 2 - 1/2" 90s, 1 - new faucet.
SHS-02-RM-IN-E236-T | 25 | 2021-05-12 | E236 | Tap in Room E236 | Faucet | Initial | 89.8 | 2021-06-15 | WO#149131. 8/4/21 - Fixture Removed.
SHS-01-CR-IN-E26-T | 5 | 2021-05-12 | E26 | Tap In Classroom E26 | Faucet | Initial | <5.00 | 2021-06-15
SHS-01-BT-IN-E26-T | 6 | 2021-05-12 | E26A | Bathroom Tap In Classroom E26 | Faucet | Initial | <5.00 | 2021-06-15
SHS-01-RM-IN-E33-T | 2 | 2021-05-12 | E33 | Tap In Room E33 | Faucet | Initial | <5.00 | 2021-06-15
SHS-01-RM-IN-SEC-T | 1 | 2021-05-12 | E34 | Tap In Security Room | Faucet | Initial | 7.65 | 2021-06-15
SHS-01-CR-IN-E6-T3 | 20 | 2021-05-12 | E6 | Right Tap In Classroom E6 | Faucet | Initial | <5.00 | 2021-06-15
SHS-01-CR-IN-E6-T2 | 21 | 2021-05-12 | E6 | Left Front Tap In Classroom E6 | Faucet | Initial | <5.00 | 2021-06-15
SHS-01-CR-IN-E6-T1 | 22 | 2021-05-12 | E6 | Left Back Tap In Classroom E6 | Faucet | Initial | <5.00 | 2021-06-15
SHS-01-CR-IN-E8-T1 | 17 | 2021-05-12 | E8 | Left Tap In Classroom E8 | Faucet | Initial | <5.00 | 2021-06-15
SHS-01-CR-IN-E8-T2 | 18 | 2021-05-12 | E8 | Middle Tap In Classroom E8 | Faucet | Initial | <5.00 | 2021-06-15
SHS-01-CR-IN-E8-T3 | 19 | 2021-05-12 | E8 | Right Tap In Classroom E8 | Faucet | Initial | <5.00 | 2021-06-15
SHS-02-HA-BY-E220-BF | 7 | 2021-05-12 | Hall by E220 | Bottle Filler Near Room E220 | Bottle Filler | Initial | <5.00 | 2021-06-15
SHS-02-HA-BY-E234-BF | 4 | 2021-05-12 | Hall by E234 | Bottle Filler Near Room E234 | Bottle Filler | Initial | <5.00 | 2021-06-15
SHS-01-HA-BY-E33-BF | 3 | 2021-05-12 | Hall by E33 | Bottle Filler Near Room E33 | Bottle Filler | Initial | <5.00 | 2021-06-15
SHS-01-HA-BY-E4-BF | 23 | 2021-05-12 | Hall by E4 | Bottle Filler By Classroom E4 | Bottle Filler | Initial | <5.00 | 2021-06-15
SHS-01-HA-BY-N100-BF | 36 | 2021-05-12 | Hall by N100 | Bottle Filler Near Room N100 | Bottle Filler | Initial | <5.00 | 2021-06-15
SHS-01-HA-BY-TR-BF1 | 46 | 2021-05-12 | Hall by S7 | Left Hand Bottle Filler Near Trainer's Room | Bottle Filler | Initial | <5.00 | 2021-06-15
SHS-01-CR-IN-N100-T | 35 | 2021-05-12 | N100 | Tap In Room N100 | Faucet | Initial | 10.2 | 2021-06-15
SHS-01-CR-IN-N101-T | 37 | 2021-05-12 | N101 | Tap In Classroom N101 | Faucet | Initial | 136 | 2021-06-15 | WO#149137. 8/14/2021 - Replaced fittings. 1 - chrome supply.
SHS-01-RM-IN-N12-T | 34 | 2021-05-12 | N12 | Tap In Room N12 | Faucet | Initial | 19.3 | 2021-06-15 | WO#149136. 8/3/21 - Fixture removed.
SHS-01-CR-IN-N18-T | 55 | 2021-05-12 | N18 | Tap In Room N18 | Faucet | Initial | 8.28 | 2021-06-15
SHS-01-CR-IN-N4-T | 38 | 2021-05-12 | N4 | Tap in Classroom N4 | Faucet | Initial | 37.3 | 2021-06-15 | WO#149138. 8/14/2021 - Replace fittings. 1 - chrome supply, 1 - 3/4" gate valve.
SHS-01-RM-IN-N9-T | 39 | 2021-05-12 | N9 | Tap In Room N9 | Faucet | Initial | 11 | 2021-06-15
SHS-01-RM-IN-NOO-T | 41 | 2021-05-12 | S5 | Tap Nurse's Office (Personal Office) | Faucet | Initial | 11.7 | 2021-06-15
SHS-01-RM-IN-NOB-T2 | 43 | 2021-05-12 | S5 | Right Tap In Nurse's Office "Bandage" Room | Faucet | Initial | 6.48 | 2021-06-15
SHS-01-RM-IN-NOB-T1 | 44 | 2021-05-12 | S5 | Left Tap In Nurse's Office "Bandage" Room | Faucet | Initial | <5.00 | 2021-06-15
SHS-01-RM-IN-TR-IM | 45 | 2021-05-12 | S7 | Trainer's Room Ice Machine | Ice Maker | Initial | <5.00 | 2021-06-15
SHS-01-RM-IN-CONC-T | 42 | 2021-05-12 | SE5A | Tap In Concessions Stand | Faucet | Initial | <5.00 | 2021-06-15
SHS-01-RM-IN-AGYM-T | 40 | 2021-05-12 | SE6 | Tap In Auxiliary Gym | Faucet | Initial | <5.00 | 2021-06-15
SHS-02-RM-IN-LAC-T | 1 | 2021-08-27 | E13 | Lactation Room Tap | Faucet | Post Remediation | 5.85 | 2021-09-03
SHS-01-CR-IN-E14-T | 3 | 2021-08-27 | E14 | Tap In Classroom E14 | Faucet | Post Remediation | 17.3 | 2021-09-03
SHS-01-CR-IN-E16-T | 2 | 2021-08-27 | E16 | Tap In Classroom E16 | Faucet | Post Remediation | 9.89 | 2021-09-03
SHS-01-RM-IN-E202-T | 4 | 2021-08-27 | E202 | Tap In Room E202 | Faucet | Post Remediation | 14.7 | 2021-09-03
SHS-01-CR-IN-N101-T | 8 | 2021-08-27 | N101 | Tap In Classroom N101 | Faucet | Post Remediation | 83.5 | 2021-09-03
SHS-01-CR-IN-N4-T | 9 | 2021-08-27 | N4 | Tap in Classroom N4 | Faucet | Post Remediation | 26.3 | 2021-09-03
SHS-01-RM-IN-TSL-T | 5 | 2021-08-27 | S2A | Tap In Teacher's Café Room Serving Line | Faucet | Post Remediation | 67.9 | 2021-09-03
SHS-01-RM-BY-EFPREP-TS | 6 | 2021-08-27 | S8 | Southern Tap Eastern Kitchen Food Prep Area | Faucet | Post Remediation | 10.9 | 2021-09-03
SHS-01-RM-BY-EFPREP-TN | 7 | 2021-08-27 | S8 | Northern Tap Eastern Kitchen Food Prep Area | Faucet | Post Remediation | 18.3 | 2021-09-03
STF-01-RM-IN-CONC-HCT | 12 | 2021-08-27 | Turf Field Concession | Turf Field Concessions Stand Hot Chocolate Tap | Hot Chocolate Tap | Post Remediation | <5.00 | 2021-09-03
STF-01-RM-IN-CONC-CT | 13 | 2021-08-27 | Turf Field Concession | Turf Field Concessions Stand Coffee Tap | Coffee Tap | Post Remediation | <5.00 | 2021-09-03
SHS-01-CR-IN-W13-T | 10 | 2021-08-27 | W13 | Tap in Room W13 | Faucet | Initial | 24.7 | 2021-09-03
SHS-02-CR-IN-W201-T | 11 | 2021-08-27 | W201 | Tap In Classroom W201 | Faucet | Post Remediation | 39.9 | 2021-09-03
SHS-01-HA-BY-E18-DF | 2 | 2022-02-24 | Hall by E14 | Drinking Fountain Near E14 | Drinking Fountain | Initial | <5.00 | 2022-03-08
SHS-01-HA-BY-E18-DF | 1 | 2022-02-24 | Hall by E18 | Drinking Fountain Near E18 | Drinking Fountain | Initial | 8.57 | 2022-03-08
SHS-01-HA-BY-N100-DF | 3 | 2022-02-24 | Hall by N100 | Drinking Fountain Near Room N100 | Drinking Fountain | Initial | <5.00 | 2022-03-08
SHS-01-HA-BY-NO-DF1 | 5 | 2022-02-24 | Hall by S5 | Left Drinking Fountain Near Nurse's Office | Drinking Fountain | Initial | <5.00 | 2022-03-08
SHS-01-HA-BY-NO-DF2 | 6 | 2022-02-24 | Hall by S5 | Right Drinking Fountain Near Nurse's Office | Drinking Fountain | Initial | <5.00 | 2022-03-08
SHS-01-HA-BY-TR-DF1 | 7 | 2022-02-24 | Hall by S7 | Left Hand Drinking Fountain Near Trainer's Room | Drinking Fountain | Initial | <5.00 | 2022-03-08
SHS-01-HA-BY-TR-DF2 | 8 | 2022-02-24 | Hall by S7 | Right Hand Drinking Fountain Near Trainer's Room | Drinking Fountain | Initial | <5.00 | 2022-03-08
SHS-02-HA-BY-W14-DF | 4 | 2022-02-24 | Hall by W14 | Drinking Fountain Near W14 | Drinking Fountain | Initial | <5.00 | 2022-03-08
SCH-01-RM-BY-E3-T | 12 | 2022-04-01 | E2 | Tap in Room E2 (Sink in Copy Room by E3) | Faucet | Initial | 7.52 | 2022-04-12
SCH-01-T-IN-PKT-T1 | 10 | 2022-04-01 | E23 | Pre-K Bathroom, Left Sink | Faucet | Initial | <5.00 | 2022-04-12 | New fixture - area renovated
SCH-01-T-IN-PKT-T2 | 11 | 2022-04-01 | E23 | Pre-K Bathroom, Right Sink | Faucet | Initial | <5.00 | 2022-04-12 | New fixture - area renovated
SCH-02-CR-IN-TC-T | 30 | 2022-04-01 | E236 | Sink in Testing Center - E236 | Faucet | Initial | 5.33 | 2022-04-12 | New fixture - area renovated
SCH-01-RM-IN-SO-T | 1 | 2022-04-01 | E34 | Sink in Security Office | Faucet | Initial | <5.00 | 2022-04-12 | New fixture - area renovated
SCH-02-HA-BY-E219-DF | 28 | 2022-04-01 | Hall by E219 | Drinking Fountain by Room E219 | Drinking Fountain | Initial | <5.00 | 2022-04-12
SCH-02-HA-BY-234E-DF | 29 | 2022-04-01 | Hall by E234 | Drinking Fountain by 234E | Drinking Fountain | Initial | <5.00 | 2022-04-12
SCH-01-HA-BY-AO-DF | 2 | 2022-04-01 | Hall by E33 | Drinking Fountain by Athletic's Office | Drinking Fountain | Initial | <5.00 | 2022-04-12
SCH-02-HA-BY-W212-DF | 26 | 2022-04-01 | Hall by W12 | Drinking Fountain by Room W12 | Drinking Fountain | Initial | <5.00 | 2022-04-12
SCH-01-HA-BY-W2-DF | 14 | 2022-04-01 | Hall by W2 | Drinking Fountain by Room W2 | Drinking Fountain | Initial | <5.00 | 2022-04-12
SCH-02-HA-BY-W200-DF | 27 | 2022-04-01 | Hall by W200 | Drinking Fountain by Room W200 | Drinking Fountain | Initial | <5.00 | 2022-04-12
SCH-01-HA-BY-W23-DF | 25 | 2022-04-01 | Hall by W23 | Drinking Fountain by Room W23 | Drinking Fountain | Initial | <5.00 | 2022-04-12
SCH-01-OFF-IN-MO-T | 13 | 2022-04-01 | N10A | Main Office Sink | Faucet | Initial | <5.00 | 2022-04-12 | New fixture - area renovated
SCH-01-RM-IN-KIT-T4 | 3 | 2022-04-01 | S8 | Western Kitchen Tap 5 (near serving area) (Sink 4 in Kitchen) | Faucet |  | <5.00 | 2022-04-12
SCH-01-BT-IN-T13-T1 | 4 | 2022-04-01 | T13 Boys Restroom | Boy's Room T-13, Sink 1 | Faucet | Initial | <5.00 | 2022-04-12 | New fixture - area renovated
SCH-01-BT-IN-T13-T2 | 5 | 2022-04-01 | T13 Boys Restroom | Boy's Room T-13, Sink 2 | Faucet | Initial | <5.00 | 2022-04-12 | New fixture - area renovated
SCH-01-BT-IN-T13-T3 | 6 | 2022-04-01 | T13 Boys Restroom | Boy's Room T-13, Sink 3 | Faucet | Initial | <5.00 | 2022-04-12 | New fixture - area renovated
SCH-01-GT-IN-T14-T1 | 7 | 2022-04-01 | T14 Girls Restroom | Girl's Room T-14, Sink 1 | Faucet | Initial | <5.00 | 2022-04-12 | New fixture - area renovated
SCH-01-GT-IN-T14-T2 | 8 | 2022-04-01 | T14 Girls Restroom | Girl's Room T-14, Sink 2 | Faucet | Initial | <5.00 | 2022-04-12 | New fixture - area renovated
SCH-01-GT-IN-T14-T3 | 9 | 2022-04-01 | T14 Girls Restroom | Girl's Room T-14, Sink 3 | Faucet | Initial | <5.00 | 2022-04-12 | New fixture - area renovated
SCH-01-GT-IN-NWGT-T1 | 20 | 2022-04-01 | T5 Girls Restroom | Northwest Girl's Gang Bathroom, Sink 1 | Faucet | Initial | <5.00 | 2022-04-12 | New fixture - area renovated
SCH-01-GT-IN-NWGT-T2 | 21 | 2022-04-01 | T5 Girls Restroom | Northwest Girl's Gang Bathroom, Sink 2 | Faucet | Initial | <5.00 | 2022-04-12 | New fixture - area renovated
SCH-01-GT-IN-NWGT-T3 | 22 | 2022-04-01 | T5 Girls Restroom | Northwest Girl's Gang Bathroom, Sink 3 | Faucet | Initial | <5.00 | 2022-04-12 | New fixture - area renovated
SCH-01-GT-IN-NWGT-T4 | 23 | 2022-04-01 | T5 Girls Restroom | Northwest Girl's Gang Bathroom, Sink 4 | Faucet | Initial | <5.00 | 2022-04-12 | New fixture - area renovated
SCH-01-GT-IN-NWGT-T5 | 24 | 2022-04-01 | T5 Girls Restroom | Northwest Girl's Gang Bathroom, Sink 5 | Faucet | Initial | <5.00 | 2022-04-12 | New fixture - area renovated
SCH-01-BT-IN-NWBT-T5 | 15 | 2022-04-01 | T6 Boys Restroom | Northwest Boy's Gang Bathroom, Sink 5 | Faucet | Initial | <5.00 | 2022-04-12 | New fixture - area renovated
SCH-01-BT-IN-NWBT-T4 | 16 | 2022-04-01 | T6 Boys Restroom | Northwest Boy's Gang Bathroom, Sink 4 | Faucet | Initial | <5.00 | 2022-04-12 | New fixture - area renovated
SCH-01-BT-IN-NWBT-T3 | 17 | 2022-04-01 | T6 Boys Restroom | Northwest Boy's Gang Bathroom, Sink 3 | Faucet | Initial | <5.00 | 2022-04-12 | New fixture - area renovated
SCH-01-BT-IN-NWBT-T2 | 18 | 2022-04-01 | T6 Boys Restroom | Northwest Boy's Gang Bathroom, Sink 2 | Faucet | Initial | <5.00 | 2022-04-12 | New fixture - area renovated
SCH-01-BT-IN-NWBT-T1 | 19 | 2022-04-01 | T6 Boys Restroom | Northwest Boy's Gang Bathroom, Sink 1 | Faucet | Initial | <5.00 | 2022-04-12 | New fixture - area renovated
SHS-02-HA-BY-W227-DF | 24 | 2022-05-20 | Hall by W227 | Hallway by W227 Drinking Fountain | Drinking Fountain | Initial | 35.5 | 2022-05-27
SHS-01-MT-IN-FAC-T | 25 | 2022-05-20 | T1 Restroom | North Mens Faculty Restroom Sink | Faucet | Initial | <5.00 | 2022-05-27
SHS-02-GT-IN-NWB-T1 | 14 | 2022-05-20 | T19 Girls Restroom | Northwest 2nd Floor Girls Restroom Sink 1 | Faucet | Initial | <5.00 | 2022-05-27
SHS-02-GT-IN-NWB-T2 | 15 | 2022-05-20 | T19 Girls Restroom | Northwest 2nd Floor Girls Restroom Sink 2 | Faucet | Initial | <5.00 | 2022-05-27
SHS-02-GT-IN-NWB-T3 | 16 | 2022-05-20 | T19 Girls Restroom | Northwest 2nd Floor Girls Restroom Sink 3 | Faucet | Initial | <5.00 | 2022-05-27
SHS-02-GT-IN-NWB-T4 | 17 | 2022-05-20 | T19 Girls Restroom | Northwest 2nd Floor Girls Restroom Sink 4 | Faucet | Initial | <5.00 | 2022-05-27
SHS-02-GT-IN-NWB-T5 | 18 | 2022-05-20 | T19 Girls Restroom | Northwest 2nd Floor Girls Restroom Sink 5 | Faucet | Initial | <5.00 | 2022-05-27
SHS-01-WT-IN-FAC-T | 26 | 2022-05-20 | T2 Restroom | North Womens Faculty Restroom Sink | Faucet | Initial | <5.00 | 2022-05-27
SHS-02-BT-IN-NWB-T5 | 19 | 2022-05-20 | T20 Boys Restroom | Northwest 2nd Floor Boys Restroom Sink 5 | Faucet | Initial | <5.00 | 2022-05-27
SHS-02-BT-IN-NWB-T4 | 20 | 2022-05-20 | T20 Boys Restroom | Northwest 2nd Floor Boys Restroom Sink 4 | Faucet | Initial | <5.00 | 2022-05-27
SHS-02-BT-IN-NWB-T3 | 21 | 2022-05-20 | T20 Boys Restroom | Northwest 2nd Floor Boys Restroom Sink 3 | Faucet | Initial | <5.00 | 2022-05-27
SHS-02-BT-IN-NWB-T2 | 22 | 2022-05-20 | T20 Boys Restroom | Northwest 2nd Floor Boys Restroom Sink 2 | Faucet | Initial | <5.00 | 2022-05-27
SHS-02-BT-IN-NWB-T1 | 23 | 2022-05-20 | T20 Boys Restroom | Northwest 2nd Floor Boys Restroom Sink 1 | Faucet | Initial | <5.00 | 2022-05-27
SHS-02-GT-IN-SEB-T1 | 8 | 2022-05-20 | T29 Girls Restroom | Southeast 2nd Floor Girls Restroom Left Sink | Faucet | Initial | <5.00 | 2022-05-27
SHS-02-GT-IN-SEB-T2 | 9 | 2022-05-20 | T29 Girls Restroom | Southeast 2nd Floor Girls Restroom Center Sink | Faucet | Initial | <5.00 | 2022-05-27
SHS-02-GT-IN-SEB-T3 | 10 | 2022-05-20 | T29 Girls Restroom | Southeast 2nd Floor Girls Restroom Right Sink | Faucet | Initial | <5.00 | 2022-05-27
SHS-02-BT-IN-SEB-T3 | 11 | 2022-05-20 | T30 Boys Restroom | Southeast 2nd Floor Boys Restroom Right Sink | Faucet | Initial | <5.00 | 2022-05-27
SHS-02-BT-IN-SEB-T2 | 12 | 2022-05-20 | T30 Boys Restroom | Southeast 2nd Floor Boys Restroom Center Sink | Faucet | Initial | <5.00 | 2022-05-27
SHS-02-BT-IN-SEB-T1 | 13 | 2022-05-20 | T30 Boys Restroom | Southeast 2nd Floor Boys Restroom Left Sink | Faucet | Initial | <5.00 | 2022-05-27
STF-01-OD-IN-FNCE-B2 | 27 | 2022-05-20 | Turf Field | Right Bubbler by Turf Field | Bubbler | Initial | <5.00 | 2022-05-27
STF-01-OD-IN-FNCE-B1 | 28 | 2022-05-20 | Turf Field | Left Bubbler by Turf Field | Bubbler | Initial | <5.00 | 2022-05-27
SCH-01-FAC-IN-E2-T | 20 | 2022-12-28 | E2 | E2 Copy Room Tap | Faucet | Initial | 7 | 2023-01-05 | New fixture - area renovated. Sampled 12/28/22
SCH-02-OF-IN-E202-T | 15 | 2022-12-28 | E202 | E202 Office Tap | Faucet | Initial | 3 | 2023-01-05 | New fixture - area renovated
SCH-02-HA-BY-W227-DF | 16 | 2022-12-28 | Hall by W227 | Hallway by W227 Drinking Fountain | Drinking Fountain | Post Remediation | <1.00 | 2023-01-05
SCH-02-HA-BY-W227-BF | 17 | 2022-12-28 | Hall by W227 | Hallway by W227 Bottle Filler | Bottle Filler | Initial | <1.00 | 2023-01-05
SCH-01-LIB-IN-KIT-T | 10 | 2022-12-28 | N18 | N18 Media Center Break Room Tap | Faucet | Initial | 8 | 2023-01-05 | New fixture - area renovated. Sampled 12/28/22
SCH-01-FACT-IN-KIT-T | 19 | 2022-12-28 | S1C | S1C Kitchen Bathroom Tap | Faucet | Initial | <1.00 | 2023-01-05 | New fixture - area renovated
SCH-01-NO-IN-TR-T | 11 | 2022-12-28 | S5 Restroom Right | S5 Nurses Office Right Bathroom Tap | Faucet | Intial | <1.00 | 2023-01-05 | New fixture - area renovated
SCH-01-NO-IN-TL-T | 12 | 2022-12-28 | S5 Restroom Left | S5 Nurses Office Left Restroom Tap | Faucet | Intial | <1.00 | 2023-01-05 | New fixture - area renovated
SCH-01-BT-IN-BBT-T1 | 1 | 2022-12-28 | T11 Boys Restroom | T11 (Gym Hall) Boys Restroom Tap 1 | Faucet | Initial | <1.00 | 2023-01-05 | New fixture - area renovated
SCH-01-BT-IN-BBT-T2 | 2 | 2022-12-28 | T11 Boys Restroom | T11 (Gym Hall) Boys Restroom Tap 2 | Faucet | Initial | <1.00 | 2023-01-05 | New fixture - area renovated
SCH-01-BT-IN-BBT-T3 | 3 | 2022-12-28 | T11 Boys Restroom | T11 (Gym Hall) Boys Restroom Tap 3 | Faucet | Initial | <1.00 | 2023-01-05 | New fixture - area renovated
SCH-01-GT-IN-GBT-T1 | 4 | 2022-12-28 | T12 Girls Restroom | T12 (Gym Hall) Girls Restroom Tap 1 | Faucet | Initial | <1.00 | 2023-01-05 | New fixture - area renovated
SCH-01-GT-IN-GBT-T2 | 5 | 2022-12-28 | T12 Girls Restroom | T12 (Gym Hall) Girls Restroom Tap 2 | Faucet | Initial | <1.00 | 2023-01-05 | New fixture - area renovated
SCH-01-GT-IN-GBT-T3 | 6 | 2022-12-28 | T12 Girls Restroom | T12 (Gym Hall) Girls Restroom Tap 3 | Faucet | Initial | <1.00 | 2023-01-05 | New fixture - area renovated
SCH-01-GT-IN-GBT-T4 | 7 | 2022-12-28 | T12 Girls Restroom | T12 (Gym Hall) Girls Restroom Tap 4 | Faucet | Initial | <1.00 | 2023-01-05 | New fixture - area renovated
SHS-01-OF-IN-W2A-T | 14 | 2022-12-28 | W2A | W2A Office Tap | Faucet | Initial | 5 | 2023-01-05 | New fixture - area renovated
SCH-02-OF-IN-W201-T | 13 | 2022-12-28 | W201 | W201 Office Tap | Faucet | Post Remediation | 19 | 2023-01-05 | Sampled 12/28/22
SCH-012-FOF-IN-W228-T | 18 | 2022-12-28 | W228 | Tap in Office W228 | Faucet | Initial | 4 | 2023-01-05 | New fixture - area renovated.
SCH-01-FAC-IN-W28-T | 9 | 2022-12-28 | W28 | Tap in Room W28 Faculty Lounge | Faucet | Initial | 14 | 2023-01-05 | New fixture - area renovated. Sampled 12/28/22
SCH-01-OF-IN-W29-T | 8 | 2022-12-28 | W29 | W29 Office Tap | Faucet | Initial | 6 | 2023-01-05 | Sampled 12/28/22
SHS-01-GT-IN-GT1-T1 | 3 | 10/12/2022 | T10 Girls Restroom | 1st Floor West Girl's Bathroom Sink 1 | Faucet | Initial | <5.00 | 2022-11-01 | New fixture - area renovated
SHS-01-GT-IN-GT1-T2 | 4 | 10/12/2022 | T10 Girls Restroom | 1st Floor West Girl's Bathroom Sink 2 | Faucet | Initial | <5.00 | 2022-11-01 | New fixture - area renovated
SHS-01-GT-IN-GT1-T3 | 5 | 10/12/2022 | T10 Girls Restroom | 1st Floor West Girl's Bathroom Sink 3 | Faucet | Initial | <5.00 | 2022-11-01 | New fixture - area renovated
SHS-01-GT-IN-GT1-T4 | 6 | 10/12/2022 | T10 Girls Restroom | 1st Floor West Girl's Bathroom Sink 4 | Faucet | Initial | <5.00 | 2022-11-01 | New fixture - area renovated
SHS-01-GT-IN-GT1-T5 | 7 | 10/12/2022 | T10 Girls Restroom | 1st Floor West Girl's Bathroom Sink 5 | Faucet | Initial | <5.00 | 2022-11-01 | New fixture - area renovated
SHS-02-WT-IN-WT2-T1 | 21 | 10/12/2022 | T21 Womens Restroom | 2nd Floor SW Women's Bathroom Left Sink | Faucet | Initial | <5.00 | 2022-11-01 | New fixture - area renovated
SHS-02-WT-IN-WT2-T2 | 22 | 10/12/2022 | T21 Womens Restroom | 2nd Floor SW Women's Bathroom Right Sink | Faucet | Initial | <5.00 | 2022-11-01 | New fixture - area renovated
SHS-02-MT-IN-MT2-T2 | 15 | 10/12/2022 | T22 Mens Restroom | 2nd Floor SW Men's Bathroom Right Sink | Faucet | Initial | <5.00 | 2022-11-01 | New fixture - area renovated
SHS-02-BT-IN-BT2-T1 | 23 | 10/12/2022 | T23 Boys Restroom | 2nd Floor SW Boy's Bathroom Sink 1 | Faucet | Initial | <5.00 | 2022-11-01 | New fixture - area renovated
SHS-02-BT-IN-BT2-T2 | 24 | 10/12/2022 | T23 Boys Restroom | 2nd Floor SW Boy's Bathroom Sink 2 | Faucet | Initial | <5.00 | 2022-11-01 | New fixture - area renovated
SHS-02-BT-IN-BT2-T3 | 25 | 10/12/2022 | T23 Boys Restroom | 2nd Floor SW Boy's Bathroom Sink 3 | Faucet | Initial | <5.00 | 2022-11-01 | New fixture - area renovated
SHS-02-BT-IN-BT2-T4 | 26 | 10/12/2022 | T23 Boys Restroom | 2nd Floor SW Boy's Bathroom Sink 4 | Faucet | Initial | <5.00 | 2022-11-01 | New fixture - area renovated
SHS-02-BT-IN-BT2-T5 | 27 | 10/12/2022 | T23 Boys Restroom | 2nd Floor SW Boy's Bathroom Sink 5 | Faucet | Initial | <5.00 | 2022-11-01 | New fixture - area renovated
SHS-02-GT-IN-GT2-T1 | 16 | 10/12/2022 | T24 Girls Restroom | 2nd Floor SW Girl's Bathroom Sink 1 | Faucet | Initial | <5.00 | 2022-11-01 | New fixture - area renovated
SHS-02-GT-IN-GT2-T2 | 17 | 10/12/2022 | T24 Girls Restroom | 2nd Floor SW Girl's Bathroom Sink 2 | Faucet | Initial | <5.00 | 2022-11-01 | New fixture - area renovated
SHS-02-GT-IN-GT2-T3 | 18 | 10/12/2022 | T24 Girls Restroom | 2nd Floor SW Girl's Bathroom Sink 3 | Faucet | Initial | <5.00 | 2022-11-01 | New fixture - area renovated
SHS-02-GT-IN-GT2-T4 | 19 | 10/12/2022 | T24 Girls Restroom | 2nd Floor SW Girl's Bathroom Sink 4 | Faucet | Initial | <5.00 | 2022-11-01 | New fixture - area renovated
SHS-02-GT-IN-GT2-T5 | 20 | 10/12/2022 | T24 Girls Restroom | 2nd Floor SW Girl's Bathroom Sink 5 | Faucet | Initial | <5.00 | 2022-11-01 | New fixture - area renovated
SHS-01-WT-IN-WT1-T1 | 8 | 10/12/2022 | T7 Womens Restroom | 1st Floor West Women's Bathroom Left Sink | Faucet | Initial | <5.00 | 2022-11-01 | New fixture - area renovated
SHS-01-WT-IN-WT1-T2 | 9 | 10/12/2022 | T7 Womens Restroom | 1st Floor West Women's Bathroom Right Sink | Faucet | Initial | <5.00 | 2022-11-01 | New fixture - area renovated
SHS-01-MT-IN-MT1-T1 | 1 | 10/12/2022 | T8 Mens Restroom | 1st Floor West Men's Bathroom Left Sink | Faucet | Initial | <5.00 | 2022-11-01 | New fixture - area renovated
SHS-01-MT-IN-MT1-T2 | 2 | 10/12/2022 | T8 Mens Restroom | 1st Floor West Men's Bathroom Right Sink | Faucet | Initial | <5.00 | 2022-11-01 | New fixture - area renovated
SHS-01-BT-IN-BT1-T1 | 10 | 10/12/2022 | T9 Boys Restroom | 1st Floor West Boy's Bathroom Sink 1 | Faucet | Initial | <5.00 | 2022-11-01 | New fixture - area renovated
SHS-01-BT-IN-BT1-T2 | 11 | 10/12/2022 | T9 Boys Restroom | 1st Floor West Boy's Bathroom Sink 2 | Faucet | Initial | <5.00 | 2022-11-01 | New fixture - area renovated
SHS-01-BT-IN-BT1-T3 | 12 | 10/12/2022 | T9 Boys Restroom | 1st Floor West Boy's Bathroom Sink 3 | Faucet | Initial | <5.00 | 2022-11-01 | New fixture - area renovated
SHS-01-BT-IN-BT1-T4 | 13 | 10/12/2022 | T9 Boys Restroom | 1st Floor West Boy's Bathroom Sink 4 | Faucet | Initial | <5.00 | 2022-11-01 | New fixture - area renovated
SHS-01-BT-IN-BT1-T5 | 14 | 10/12/2022 | T9 Boys Restroom | 1st Floor West Boy's Bathroom Sink 5 | Faucet | Initial | <5.00 | 2022-11-01 | New fixture - area renovated

## Thomas HS
Date Last Updated |  | 2022-05-26
School Name: |  | Thomas High School
Lab ELAP ID# |  | NY63556 |  |  |  | Method of Analysis: |  |  | Metals 200.9
Lab ID# | School Sample ID # | Collection Date | Sample Location | Sample Location Description | Outlet Description | Initial/ Post Remediation | Lead Result mcg/L (ppb) | Lab Report Reciept Date | Action Taken for Outlets Greater than 15 mcg/L
THS-01-CR-IN-145-T | 77 | 2021-05-19 | 145 | Tap In Classroom 145 | Faucet | Initial | <5.00 | 2021-06-15
THS-01-RM-IN-236-T | 81 | 2021-05-19 | 236 | Tap In Room 236 | Faucet | Initial | <5.00 | 2021-06-15
THS-01-RM-IN-240-T | 105 | 2021-05-19 | 240 | Tap In Room 240 | Faucet | Initial | 6.34 | 2021-06-15
THS-01-RM-IN-248-T | 80 | 2021-05-19 | 248 | Tap In Room 248 | Faucet | Initial | 9.67 | 2021-06-15
THS-01-RM-IN-251-T | 79 | 2021-05-19 | 251 | Tap In Room 251 | Faucet | Initial | 6.27 | 2021-06-15
THS-01-CR-IN-303-IM | 78 | 2021-05-19 | 303 | Classroom 303 Ice Machine | Ice Maker | Initial | <5.00 | 2021-06-15
THS-01-CR-IN-311-T | 48 | 2021-05-19 | 311 | Tap In Classroom 311 | Faucet | Initial | <5.00 | 2021-06-15
THS-01-RM-IN-332-T | 52 | 2021-05-19 | 332 | Tap In Room 332 | Faucet | Initial | <5.00 | 2021-06-15
THS-01-CR-IN-334-T2 | 54 | 2021-05-19 | 334 | Right Tap In Classroom 334 | Faucet | Initial | <5.00 | 2021-06-15
THS-01-CR-IN-334-T1 | 55 | 2021-05-19 | 334 | Left Tap In Classroom 334 | Faucet | Initial | <5.00 | 2021-06-15
THS-01-CR-IN-336-T1 | 56 | 2021-05-19 | 336 | Left Tap In Classroom 336 | Faucet | Initial | 5.87 | 2021-06-15
THS-01-CR-IN-336-T2 | 57 | 2021-05-19 | 336 | Right Tap In Classroom 336 | Faucet | Initial | 9.61 | 2021-06-15
THS-01-CR-IN-338-T1 | 58 | 2021-05-19 | 338 | Left Tap In Classroom 338 | Faucet | Initial | 10.4 | 2021-06-15
THS-01-CR-IN-338-T2 | 59 | 2021-05-19 | 338 | Right Tap In Classroom 338 | Faucet | Initial | 6.92 | 2021-06-15
THS-01-RM-BY-338-T | 60 | 2021-05-19 | 338 | Tap By Classroom 338 (side room) | Faucet | Initial | 15.2 | 2021-06-15 | WO#149153 - 8/26/21. Labeled "Non-Potable Water. Not for Drinking or Cooking Use"
THS-01-CR-IN-340-T1 | 61 | 2021-05-19 | 340 | Classroom 340 Left Tap | Faucet | Initial | 9.91 | 2021-06-15
THS-01-CR-IN-340-T2 | 62 | 2021-05-19 | 340 | Classroom 340 Middle Tap | Faucet | Initial | 7.83 | 2021-06-15
THS-01-CR-IN-340-T3 | 63 | 2021-05-19 | 340 | Classroom 340 Right Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-BT1-IN-422-T | 2 | 2021-05-18 | 422 | Left Restroom Tap In Room 422 | Faucet | Initial | 11.4 | 2021-06-15
THS-01-BT3-IN-422-T | 3 | 2021-05-18 | 422 | Right Restroom Tap In Room 422 | Faucet | Initial | 32.4 | 2021-06-15 | WO#149143 - 8/26/21. Labeled "Non-Potable Water. Not for Drinking or Cooking Use"
THS-01-RM-IN-422-T1 | 4 | 2021-05-18 | 422 | Tap In Room 422 Closest to Hallway (Left Tap) | Faucet | Initial | 6.41 | 2021-06-15
THS-01-RM-IN-422-T2 | 5 | 2021-05-18 | 422 | Tap In Room 422 Furthest From Hallway (Right Tap) | Faucet | Initial | 17.5 | 2021-06-15 | WO#149144. 8/25/21 - Replaced fittings, 1 - 1/2" brass valve, 5 - 1/2" 90s, 1 - 1/2" T, 1 - 1/2"x3/8" compression, 1 - 1/2" ball valve, 1- 3/8" x 12" supply line.
THS-01-RM-IN-422-IM | 6 | 2021-05-18 | 422 | Ice Machine In Room 422 | Ice Maker | Initial | <5.00 | 2021-06-15
THS-01-RM-IN-422-T2 | 17 | 2021-08-27 | 422 | Tap In Room 422 Furthest From Hallway (Right Tap) | Faucet | Post Remediation | 14.1 | 2021-09-03
THS-01-RM-IN-TR-T | 31 | 2021-05-18 | 451 | Training Room Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-RM-IN-TR-IM | 32 | 2021-05-18 | 451 | Training Room Ice Machine | Ice Maker | Initial | <5.00 | 2021-06-15
THS-01-RM-IN-454-T | 36 | 2021-05-18 | 454 | Room 454 Tap | Faucet | Initial | 17.7 | 2021-06-15 | WO#149151 - 8/26/21. Flush and install new aerator.
THS-01-RM-IN-454-T | 20 | 2021-08-27 | 454 | Room 454 Tap | Faucet | Post Remediation | 11.1 | 2021-09-03
THS-01-GT-IN-328-T | 49 | 2021-05-19 | 328 Womens Restroom | Women's Restroom Tap In Room 328 | Faucet | Initial | <5.00 | 2021-06-15
THS-01-BT-IN-330-T | 51 | 2021-05-19 | 330 Mens Restroom | Men's Restroom Tap In Room 330 | Faucet | Initial | 6.06 | 2021-06-15
THS-01-RM-BY-KIPREP-T2 | 15 | 2021-05-18 | 445 Kitchen | Kitchen Prep Area Right Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-RM-BY-KISRVN-T | 17 | 2021-05-18 | 445 Kitchen | Tap Near Northern Serving Area In Kitchen | Faucet | Initial | <5.00 | 2021-06-15
THS-01-RM-IN-KI-PF1 | 18 | 2021-05-18 | 445 Kitchen | Kitchen Left Hand Pot Filler | Pot Filler | Initial | <5.00 | 2021-06-15
THS-01-RM-IN-KI-PF2 | 19 | 2021-05-18 | 445 Kitchen | Kitchen Right Hand Pot Filler | Pot Filler | Initial | 5.34 | 2021-06-15
THS-01-RM-IN-KI-T3 | 21 | 2021-05-18 | 445 Kitchen | Kitchen Southeast Corner Right Sink | Faucet | Initial | 21.2 | 2021-06-15 | WO#149145 - 8/26/21. Labeled "Non-Potable Water. Not for Drinking or Cooking Use"
THS-01-RM-IN-KI-T1 | 22 | 2021-05-18 | 445 Kitchen | Kitchen Southeast Corner Left Sink | Faucet | Initial | 9.94 | 2021-06-15
THS-01-RM-IN-DW-T1 | 23 | 2021-05-18 | 445 Kitchen | Dishwashing Area Left Tap | Faucet | Initial | 5.03 | 2021-06-15
THS-01-RM-IN-DW-T2 | 24 | 2021-05-18 | 445 Kitchen | Dishwashing Area Right Tap | Faucet | Initial | 11.1 | 2021-06-15
THS-01-RM-IN-KI-CT2 | 25 | 2021-05-18 | 445 Kitchen | Right Coffee Tap | Coffe Tap | Initial | 47.4 | 2021-06-15 | WO#149146. 8/21/21. Remove ball valve, Replace 1 single chrome stop, 3/8" x 30" supply lines.
THS-01-RM-IN-KI-CT1 | 26 | 2021-05-18 | 445 Kitchen | Left Coffee Tap | Coffe Tap | Initial | 20.5 | 2021-06-15 | WO#149147. 8/21/21. Remove ball valve, lines and T. Replace 1 chrome stop, 2 - 3/8" supply lines.
THS-01-RM-BY-KIPREP-T1 | 16 | 2021-05-19 | 445 Kitchen | Kitchen Prep Area Left Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-RM-IN-KI-T2 | 20 | 2021-05-19 | 445 Kitchen | Kitchen East Standalone Sink | Faucet | Initial | <5.00 | 2021-06-15
THS-01-RM-IN-KI-CT2 | 18 | 2021-08-27 | 445 Kitchen | Right Coffee Tap | Coffe Tap | Post Remediation | 9.08 | 2021-09-03
THS-01-RM-IN-KI-CT1 | 19 | 2021-08-27 | 445 Kitchen | Left Coffee Tap | Coffe Tap | Post Remediation | 10.7 | 2021-09-03
THS-01-BT-IN-KI-T | 27 | 2021-05-18 | 445C | Kitchen Bathroom Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-BT-IN-MLR-T | 28 | 2021-05-18 | 449C | Male Coach's Locker Room Bathroom Tap | Faucet | Initial | 7.27 | 2021-06-15
THS-01-BT-IN-BLR-T1 | 29 | 2021-05-18 | 449H | Boy's Locker Room Bathroom Left Tap | Faucet | Initial | 17.6 | 2021-06-15 | WO#149148 - 8/21/21. Labeled "Non-Potable Water. Not for Drinking or Cooking Use"
THS-01-BT-IN-BLR-T2 | 30 | 2021-05-18 | 449H | Boy's Locker Room Bathroom Right Tap | Faucet | Initial | 61 | 2021-06-15 | WO#149149 - 8/21/21. Labeled "Non-Potable Water. Not for Drinking or Cooking Use"
THS-01-GT-IN-GLR-T2 | 45 | 2021-05-18 | 451 Restroom | Girls Locker Room Bathroom Right Tap | Faucet | Initial | 12.8 | 2021-06-15
THS-01-GT-IN-GLR-T1 | 46 | 2021-05-18 | 451 Restroom | Girls Locker Room Bathroom Left Tap | Faucet | Initial | 22.1 | 2021-06-15 | WO#149152 - 8/26/21. Labeled "Non-Potable Water. Not for Drinking or Cooking Use"
THS-01-BT-IN-452-T | 33 | 2021-05-18 | 452 Restroom | Tap In Restroom (Room 452) | Faucet | Initial | 10.7 | 2021-06-15
THS-01-BT-IN-454-T1 | 34 | 2021-05-18 | 454 Boys Restroom | Boys Restroom In Room 454 Left Tap | Faucet | Initial | 15.2 | 2021-06-15 | WO#149150 - 8/21/21. Labeled "Non-Potable Water. Not for Drinking or Cooking Use"
THS-01-BT-IN-454-T2 | 35 | 2021-05-18 | 454 Boys Restroom | Boys Restroom In Room 454 Right Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-RM-IN-POOL-DF | 9 | 2022-02-23 | 465 Pool | Pool Drinking Fountain | Drinking Fountain | Initial | <5.00 | 2022-03-08
THS-01-POOL-IN-POOL-DF | 1 | 2022-03-31 | 465 Pool | Drinking Fountain in Pool | Drinking Fountain | Initial | <5.00 | 2022-04-12
THS-01-HA-BY-POOL-DF | 2 | 2022-03-31 | 465 Pool | Drinking Fountain by Pool | Drinking Fountain | Initial | <5.00 | 2022-04-12
THS-01-GT-IN-WLR-T | 47 | 2021-05-18 | 466B | Women's Locker Room Bathroom Tap | Faucet | Initial | 10.1 | 2021-06-15
THS-01-RM-IN-FHNE-BF | 97 | 2021-05-18 | 470 Field House | Northeast Corner of Field House Bottle Filler | Faucet | Initial | <5.00 | 2021-06-15
THS-01-RM-IN-FHNW-DF2 | 5 | 2022-02-23 | 470 Field House | Northwest Corner of Field House Right Drinking Fountain | Drinking Fountain | Initial | <5.00 | 2022-03-08
THS-01-RM-IN-FHNW-DF1 | 6 | 2022-02-23 | 470 Field House | Northwest Corner of Field House Left Drinking Fountain | Drinking Fountain | Initial | <5.00 | 2022-03-08
THS-01-RM-IN-FHNE-DF1 | 7 | 2022-02-23 | 470 Field House | Northeast Corner of Field House Left Drinking Fountain | Drinking Fountain | Initial | <5.00 | 2022-03-08
THS-01-RM-IN-FHNE-DF2 | 8 | 2022-02-23 | 470 Field House | Northeast Corner of Field House Right Drinking Fountain | Drinking Fountain | Initial | <5.00 | 2022-03-08
THS-01-RM-IN-CONC-T | 96 | 2021-05-18 | 470B | Tap In Concessions Stand | Faucet | Initial | <5.00 | 2021-06-15
THS-01-GT-BY-GYM-T3 | 93 | 2021-05-18 | 470C Girls Restroom | Girls Restroom By Gym Right Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-GT-BY-GYM-T2 | 94 | 2021-05-18 | 470C Girls Restroom | Girls Restroom By Gym Middle Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-GT-BY-GYM-T1 | 95 | 2021-05-18 | 470C Girls Restroom | Girls Restroom By Gym Left Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-BT-BY-GYM-T1 | 89 | 2021-05-18 | 470D Boys Restroom | Boys Restroom By Gym Left Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-BT-BY-GYM-T2 | 90 | 2021-05-18 | 470D Boys Restroom | Boys Restroom By Gym Middle Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-BT-BY-GYM-T3 | 91 | 2021-05-18 | 470D Boys Restroom | Boys Restroom By Gym Right Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-RM-IN-FBR-T | 53 | 2021-05-19 | A134 | Faculty Break Room | Faucet | Initial | 5.8 | 2021-06-15
THS-01-RM-BY-139-T | 76 | 2021-05-19 | A134 | Tap By Room 139 (Teacher's Lounge Tap via Bathroom) | Faucet | Initial | <5.00 | 2021-06-15
THS-01-GT-BY-139-T2 | 74 | 2021-05-19 | A135 Womens Restroom | Women's Restroom Right Tap By Room 139 | Faucet | Initial | <5.00 | 2021-06-15
THS-01-GT-BY-139-T1 | 75 | 2021-05-19 | A135 Womens Restroom | Women's Restroom Left Tap By Room 139 | Faucet | Initial | <5.00 | 2021-06-15
THS-01-BT-BY-139-T | 73 | 2021-05-19 | A140 Mens Restroom | Men's Restroom Tap By Room 139 | Faucet | Initial | 6.13 | 2021-06-15
THS-01-RM-IN-MO-T | 72 | 2021-05-19 | A146 Main Office | Tap In Main Office | Faucet | Initial | 33.5 | 2021-06-15 | WO#149154 - 8/26/21. Labeled "Non-Potable Water. Not for Drinking or Cooking Use"
THS-01-RM-IN-MO-T | 21 | 2021-08-27 | A146 Main Office | Tap In Main Office | Faucet | Post Remediation | 25.8 | 2021-09-03
THS-01-BT-BY-107-T | 99 | 2021-05-19 | A159A | Bathroom By Room 107 Tap | Faucet | Initial | 13.9 | 2021-06-15
THS-01-BT-BY-128-T | 98 | 2021-05-19 | A159C | Bathroom By Room 128 Tap | Faucet | Initial | 15.4 | 2021-06-15 | WO#149155 - 8/26/21. Labeled "Non-Potable Water. Not for Drinking or Cooking Use"
THS-01-BT-BY-200-T1 | 100 | 2021-05-19 | Boys Restroom by 200 | Boys Restroom By Room 200 Left Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-BT-BY-200-T2 | 102 | 2021-05-19 | Boys Restroom by 200 | Boys Restroom By Room 200 Right Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-BT-BY-454-T1 | 37 | 2021-05-18 | Boys Restroom by Gym | Restroom By Room 454 Left Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-BT-BY-454-T2 | 38 | 2021-05-18 | Boys Restroom by Gym | Restroom By Room 454 Middle Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-BT-BY-454-T3 | 39 | 2021-05-18 | Boys Restroom by Gym | Restroom By Room 454 Right Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-BT-BY-236-T1 | 83 | 2021-05-19 | C119 Boys Restroom | Boys Bathroom Near Room 236 Left Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-BT-BY-236-T2 | 85 | 2021-05-19 | C119 Boys Restroom | Boys Bathroom Near Room 236 Middle Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-BT-BY-236-T3 | 87 | 2021-05-19 | C119 Boys Restroom | Boys Bathroom Near Room 236 Right Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-GT-BY-236-T3 | 84 | 2021-05-19 | C120 Girls Restroom | Girls Bathroom Near Room 236 Right Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-GT-BY-236-T2 | 86 | 2021-05-19 | C120 Girls Restroom | Girls Bathroom Near Room 236 Middle Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-GT-BY-236-T1 | 88 | 2021-05-19 | C120 Girls Restroom | Girls Bathroom Near Room 236 Left Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-CR-IN-REC-T | 1 | 2021-05-18 | C243 | Receiving Room Tap | Faucet | Initial | <5.00 | 2021-06-15
TTF-01-RM-IN-CONC-T | 106 | 2021-05-19 | Concession Stand - Outdoors | Tap In Outdoor Concessions Stand | Faucet | Initial | 5.93 | 2021-06-15
TTF-01-RM-IN-CONC-CT | 107 | 2021-05-19 | Concession Stand - Outdoors | Coffee Tap In Outdoor Concessions Stand | Coffe Tap | Initial | 11.2 | 2021-06-15
THS-01-GT-BY-402-T3 | 69 | 2021-05-19 | F141 Girls Restroom | Girls Restroom By Room 402 Right Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-GT-BY-402-T2 | 70 | 2021-05-19 | F141 Girls Restroom | Girls Restroom By Room 402 Middle Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-GT-BY-402-T1 | 71 | 2021-05-19 | F141 Girls Restroom | Girls Restroom By Room 402 Left Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-BT-BY-402-T1 | 64 | 2021-05-19 | F142 Boys Restroom | Boys Restroom By Room 402 Left Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-BT-BY-402-T2 | 65 | 2021-05-19 | F142 Boys Restroom | Boys Restroom By Room 402 Middle Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-BT-BY-402-T3 | 66 | 2021-05-19 | F142 Boys Restroom | Boys Restroom By Room 402 Right Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-GT-BY-200-T2 | 101 | 2021-05-19 | Girls Restroom by 200 | Girls Restroom By Room 200 Right Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-GT-BY-200-T1 | 103 | 2021-05-19 | Girls Restroom by 200 | Girls Restroom By Room 200 Left Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-GT-BY-454-T3 | 42 | 2021-05-18 | Girls Restroom by Gym | Girls Restroom Near Room 454 Right Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-GT-BY-454-T2 | 43 | 2021-05-18 | Girls Restroom by Gym | Girls Restroom Near Room 454 Middle Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-GT-BY-454-T1 | 44 | 2021-05-18 | Girls Restroom by Gym | Girls Restroom Near Room 454 Left Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-HA-BY-212-BF | 104 | 2021-05-19 | Hall by 212 | Bottle Filler Near Room 212 | Faucet | Initial | <5.00 | 2021-06-15
THS-01-HA-BY-212-DF | 10 | 2022-02-23 | Hall by 212 | Drinking Fountain Near Room 212 | Drinking Fountain | Initial | <5.00 | 2022-03-08
THS-01-HA-BY-BHO-DF | 5 | 2022-03-31 | Hall by 212 | Drinking Fountain by Blue House Office | Drinking Fountain | Initial | <5.00 | 2022-04-12
THS-01-HA-BY-236-BF | 82 | 2021-05-19 | Hall by 236 | Bottle FIller Near Room 236 | Bottle Filler | Initial | <5.00 | 2021-06-15
THS-01-HA-BY-236-DF | 4 | 2022-03-31 | Hall by 236 | Drinking Fountain by Room 236 | Drinking Fountain | Initial | <5.00 | 2022-04-12
THS-01-HA-BY-WLIB-DF1 | 11 | 2022-02-23 | Hall by 254 | Left Drinking Fountain Near West Library | Drinking Fountain | Initial | <5.00 | 2022-03-08
THS-01-HA-BY-WLIB-DF2 | 12 | 2022-02-23 | Hall by 254 | Right Drinking Fountain Near West Library | Drinking Fountain | Initial | <5.00 | 2022-03-08
THS-01-HA-BY-328-BF | 50 | 2021-05-19 | Hall by 328 | Bottle Filler Near Room 328 | Bottle Filler | Initial | <5.00 | 2021-06-15
THS-01-HA-BY-FAC-DF | 3 | 2022-03-31 | Hall by 328 | Drinking Fountain by Faculty Room | Drinking Fountain | Initial | <5.00 | 2022-04-12
THS-01-HA-BY-402-BF2 | 67 | 2021-05-19 | Hall by 402 | Right Hand Bottle Filler By Room 402 | Bottle Filler | Initial | <5.00 | 2021-06-15
THS-01-HA-BY-402-BF1 | 68 | 2021-05-19 | Hall by 402 | Left Hand Bottle Filler By Room 402 | Bottle Filler | Initial | <5.00 | 2021-06-15
THS-01-HA-BY-SCAFE-BF1 | 10 | 2021-05-18 | Hall by 443 Cafe | Left Hand Bottle Filler By South Café | Bottle Filler | Initial | <5.00 | 2021-06-15
THS-01-HA-BY-SCAFE-BF2 | 11 | 2021-05-18 | Hall by 443 Cafe | Right Hand Bottle Filler By South Café | Bottle Filler | Initial | <5.00 | 2021-06-15
THS-01-HA-BY-SCAFE-DF1 | 1 | 2022-02-23 | Hall by 443 Cafe | Left Hand Drinking Fountain By South Café | Drinking Fountain | Initial | <5.00 | 2022-03-08
THS-01-HA-BY-SCAFE-DF2 | 2 | 2022-02-23 | Hall by 443 Cafe | Right Hand Drinking Fountain By South Café | Drinking Fountain | Initial | <5.00 | 2022-03-08
THS-01-HA-BY-454-BF1 | 40 | 2021-05-18 | Hall by 454 | Left Bottle Filler Near Room 454 | Bottle Filler | Initial | <5.00 | 2021-06-15
THS-01-HA-BY-454-BF2 | 41 | 2021-05-18 | Hall by 454 | Right Bottle Filler Near Room 454 | Bottle Filler | Initial | <5.00 | 2021-06-15
THS-01-HA-BY-GYM-BF | 92 | 2021-05-18 | Hall by 470 Restrooms | Bottle Filler By Gym | Faucet | Initial | <5.00 | 2021-06-15
THS-01-HA-BY-MO-DF1 | 6 | 2022-03-31 | Hall by A146 Main Office | Left Drinking Fountain by Main Office | Drinking Fountain | Initial | <5.00 | 2022-04-12
THS-01-HA-BY-MO-DF2 | 7 | 2022-03-31 | Hall by A146 Main Office | Right Drinking Fountain by Main Office | Drinking Fountain | Initial | <5.00 | 2022-04-12
THS-01-HA-BY-GYM-DF | 3 | 2022-02-23 | Hall by Gym | Drinking Fountain By Gym | Drinking Fountain | Initial | <5.00 | 2022-03-08
THS-01-HA-BY-GYM-DF2 | 4 | 2022-02-23 | Hall by Gym | Drinking Fountain by Gym? | Drinking Fountain | Initial | <5.00 | 2022-03-08
THS-01-GT-BY-SCAFE-T3 | 12 | 2021-05-18 | T122 Girls Restroom | Girls Restroom By South Café Right Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-GT-BY-SCAFE-T1 | 14 | 2021-05-18 | T122 Girls Restroom | Girls Restroom By South Café Left Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-GT-BY-SCAFE-T2 | 13 | 2021-05-19 | T122 Girls Restroom | Girls Restroom By South Café Middle Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-BT-BY-SEC-T1 | 7 | 2021-05-18 | T123 Boys Restroom | Boys Restroom By Security Left Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-BT-BY-SEC-T2 | 8 | 2021-05-18 | T123 Boys Restroom | Boys Restroom By Security Middle Tap | Faucet | Initial | <5.00 | 2021-06-15
THS-01-BT-BY-SEC-T3 | 9 | 2021-05-18 | T123 Boys Restroom | Boys Restroom By Security Right Tap | Faucet | Initial | <5.00 | 2021-06-15
TTF-01-OD-BY-TURF-SP | 108 | 2021-05-19 | Turf Field | Spigot By Turf Field | Spigot | Initial | <5.00 | 2021-06-15
TTF-01-OD-IN-FNCE-B1 | 4 | 2022-05-20 | Turf Field | Turf Field Left Bubbler | Drinking Fountain | Initial | <5.00 | 2022-05-26
TTF-01-OD-IN-FNCE-B2 | 5 | 2022-05-20 | Turf Field | Turf Field Right Bubbler | Drinking Fountain | Initial | 44.1 | 2022-05-26

## Basket Road
Date Last Updated |  | 2022-05-26
School Name: |  | Basket Road
Lab ELAP ID# |  | NY63556 |  |  | Method of Analysis: |  |  | Metals 200.9
Lab ID# | School Sample ID # | Collection Date | Sample Location | Outlet Description | Initial/ Post Remediation | Lead Result mcg/L (ppb) | Lab Report Reciept Date | Action Taken for Outlets Greater than 15 mcg/L
BRD-01-RM-IN-DGOUTE-B | 6 | 2022-05-20 | Eastern Dugout Bubbler | Bubbler | Initial | 8.65 | 2022-05-27
BRD-01-RM-IN-DGOUTW-B | 7 | 2022-05-20 | Western Dugout Bubbler | Bubbler | Initial | <5.00 | 2022-05-27

## Aquatic Center
Date Last Updated |  | 2022-03-09
School Name: |  | Aquatic Center
Lab ELAP ID# |  | NY63556 |  |  |  | Method of Analysis: |  |  | Metals 200.9
Lab ID# | School Sample ID # | Collection Date | Sample Location | Sample Location Description | Outlet Description | Initial/ Post Remediation | Lead Result mcg/L (ppb) | Lab Report Reciept Date | Action Taken for Outlets Greater than 15 mcg/L
WAC-01-RM-IN-POOL-BF | 1 | 2021-05-04 | SE17 | Bottle Filler In Pool Area | Bottle Filler | Initial | <5.00 | 2021-06-15
WAC-01-RM-IN-MLR-T1 | 2 | 2021-05-04 | SE14 | Men's Locker Room Left Tap | Faucet | Initial | <5.00 | 2021-06-15
WAC-01-RM-IN-MLR-T2 | 3 | 2021-05-04 | SE14 | Men's Locker Room Right Tap | Faucet | Initial | <5.00 | 2021-06-15
WAC-01-RM-IN-WLR-T1 | 4 | 2021-05-04 | SE11 | Women's Locker Room Left Tap | Faucet | Initial | <5.00 | 2021-06-15
WAC-01-RM-IN-WLR-T2 | 5 | 2021-05-04 | SE11 | Women's Locker Room Right Tap | Faucet | Initial | <5.00 | 2021-06-15
WAC-01-RM-IN-MLRS-T2 | 6 | 2021-05-04 | SE8 | Men's Southern Locker Room Right Tap | Faucet | Initial | <5.00 | 2021-06-15
WAC-01-RM-IN-MLRS-T1 | 7 | 2021-05-04 | SE8 | Men's Southern Locker Room Left Tap | Faucet | Initial | <5.00 | 2021-06-15
WAC-01-RM-IN-WLRS-T1 | 8 | 2021-05-04 | SE3 | Women's Southern Locker Room Left Tap | Faucet | Initial | <5.00 | 2021-06-15
WAC-01-RM-IN-WLRS-T2 | 9 | 2021-05-04 | SE8 | Women's Southern Locker Room Right Tap | Faucet | Initial | <5.00 | 2021-06-15
WAC-01-RM-IN-CONC-T | 10 | 2021-05-04 | SE35 | Tap In Concessions Stand | Faucet | Initial | <5.00 | 2021-06-15
WAC-01-RM-IN-FA-T | 11 | 2021-05-04 | SE27 | Tap In First Aid Room | Faucet | Initial | <5.00 | 2021-06-15
WAC-01-RM-IN-FA-IM | 12 | 2021-05-04 | SE27 | Ice Machine In First Aid Room | Ice Machine | Initial | <5.00 | 2021-06-15
WAC-01-RM-IN-LGB-T | 13 | 2021-05-04 | SE28 | Life Guard Bathroom Tap | Faucet | Initial | <5.00 | 2021-06-15
WAC-01-RM-IN-GT-T1 | 14 | 2021-05-04 | SE29 | 1st Floor Girls Bathroom Left Tap | Faucet | Initial | <5.00 | 2021-06-15
WAC-01-RM-IN-GT-T2 | 15 | 2021-05-04 | SE29 | 1st Floor Girls Bathroom Middle Tap | Faucet | Initial | <5.00 | 2021-06-15
WAC-01-RM-IN-GT-T3 | 16 | 2021-05-04 | SE29 | 1st Floor Girls Bathroom Right Tap | Faucet | Initial | <5.00 | 2021-06-15
WAC-01-RM-IN-BT-T3 | 17 | 2021-05-04 | SE30 | 1st Floor Boys Bathroom Right Tap | Faucet | Initial | <5.00 | 2021-06-15
WAC-01-RM-IN-BT-T2 | 18 | 2021-05-04 | SE30 | 1st Floor Boys Bathroom Middle Tap | Faucet | Initial | <5.00 | 2021-06-15
WAC-01-RM-IN-BT-T1 | 19 | 2021-05-04 | SE30 | 1st Floor Boys Bathroom Left Tap | Faucet | Initial | <5.00 | 2021-06-15
WAC-01-HA-BY-FD-BF | 20 | 2021-05-04 | 1st Floor by Front Door | 1st Floor Front Door Bottle Filler | Bottle Filler | Initial | <5.00 | 2021-06-15
WAC-02-RM-IN-GT-T1 | 21 | 2021-05-04 | SE42 | 2nd Floor Girls Bathroom Left Tap | Faucet | Initial | <5.00 | 2021-06-15
WAC-02-RM-IN-GT-T2 | 22 | 2021-05-04 | SE42 | 2nd Floor Girls Bathroom Middle Tap | Faucet | Initial | <5.00 | 2021-06-15
WAC-02-RM-IN-GT-T3 | 23 | 2021-05-04 | SE42 | 2nd Floor Girls Bathroom Right Tap | Faucet | Initial | <5.00 | 2021-06-15
WAC-02-RM-IN-BT-T3 | 24 | 2021-05-04 | SE41 | 2nd Floor Boys Bathroom Right Tap | Faucet | Initial | <5.00 | 2021-06-15
WAC-02-RM-IN-BT-T2 | 25 | 2021-05-04 | SE41 | 2nd Floor Boys Bathroom Middle Tap | Faucet | Initial | <5.00 | 2021-06-15
WAC-02-RM-IN-BT-T1 | 26 | 2021-05-04 | SE41 | 2nd Floor Boys Bathroom Left Tap | Faucet | Initial | <5.00 | 2021-06-15
WAC-02-HA-BY-FD-BF | 27 | 2021-05-04 | 2nd Floor Hall | 2nd Floor Front Door Bottle Filler | Bottle Filler | Initial | <5.00 | 2021-06-15
WAC-01-RM-IN-POOL-DF | 1 | 2022-02-24 | SE17 | Drinking Fountain In Pool Area | Drinking Fountain | Initial | <5.00 | 2022-03-08
WAC-01-HA-BY-LRS-DF | 2 | 2022-02-24 | 1st Floor Hall by Locker Rooms | Drinking Fountain In Locker Rooms Hallway | Drinking Fountain | Initial | <5.00 | 2022-03-08
WAC-01-HA-BY-FD-DF | 3 | 2022-02-24 | 1st Floor by Front Door | 1st Floor Front Door Drinking Fountain | Drinking Fountain | Initial | <5.00 | 2022-03-08
WAC-02-HA-BY-FD-DF | 4 | 2022-02-24 | 2nd Floor Hall | 2nd Floor Front Door Drinking Fountain | Drinking Fountain | Initial | <5.00 | 2022-03-08

## Buildings & Grounds
Date Last Updated |  | 2021-09-09
School Name: |  | Buildings and Grounds
Lab ELAP ID# |  | NY63556 |  |  |  | Method of Analysis: |  |  | Metals 200.9
Lab ID# | School Sample ID # | Collection Date | Sample Location | Sample Location Description | Outlet Description | Initial/ Post Remediation | Lead Result mcg/L (ppb) | Lab Report Reciept Date | Action Taken for Outlets Greater than 15 mcg/L
WBG1-01-GT-BY-107-T | 1 | 2021-05-05 | 105 | Building 1 Women's Restroom Tap Near Room 107 | Faucet | Initial | <5.00 | 2021-06-15
WBG1-01-HA-BY-107-BF | 2 | 2021-05-05 | Hall by 106 | Building 1 Bottle Filler Near Room 107 | Bottle Filler | Initial | <5.00 | 2021-06-15
WBG1-01-BT-BY-103A-T | 3 | 2021-05-05 | 104 | Building 1 Men's Restroom Tap Near Room 103A | Faucet | Initial | <5.00 | 2021-06-15
WBG1-01-BT-IN-TECH-T | 4 | 2021-05-05 | C100 Mens Room | Building 1 Men's Restroom Tap In Tech Area | Faucet | Initial | <5.00 | 2021-06-15
WBG1-01-GT-IN-TECH-T | 5 | 2021-05-05 | C100 Womens Room | Building 1 Women's Restroom Tap In Tech Area | Faucet | Initial | <5.00 | 2021-06-15
WBG1-01-RM-IN-TECH-BF | 6 | 2021-05-05 | 137 | Building 1 Bottle Filler In Tech Area | Bottle Filler | Initial | <5.00 | 2021-06-15
WBG1-01-RM-IN-KIT-CT | 7 | 2021-05-05 | 138 | Tech Area Kitchen Coffee Tap | Coffee Tap | Initial | 22.8 | 2021-06-15 | WO#149156. 8/27/21. New filter installed.
WBG1-01-RM-IN-KIT-CT | 15 | 2021-08-27 | 138 | Tech Area Kitchen Coffee Tap | Coffee Tap | Post Remediation | <5.00 | 2021-09-03
WBG1-01-RM-IN-KIT-T | 8 | 2021-05-05 | 138 | Building 1 Kitchen Tap (In Tech Area) | Faucet | Initial | <5.00 | 2021-06-15
WBG2-01-RM-BY-COFF-T | 9 | 2021-05-05 | 121 | Building 2 Tap Near Construction Office | Faucet | Initial | <5.00 | 2021-06-15
WBG3-01-BT-BY-MECH-T | 10 | 2021-05-05 | Building 3 Mens Room | Building 3 Men's Restroom Tap Near Mechanical Room | Faucet | Initial | <5.00 | 2021-06-15
WBG3-01-GT-BY-MECH-T | 11 | 2021-05-05 | Building 3 Womens Room | Building 3 Women's Restroom Tap Near Mechanical Room | Faucet | Initial | 5.08 | 2021-06-15
WBG3-01-HA-BY-MECH-BF | 12 | 2021-05-05 | Building 3 Bottle Filler | Building 3 Bottle Filler Near Mechanical Room | Bottle Filler | Initial | <5.00 | 2021-06-15
WBG3-01-RM-IN-KIT-T | 13 | 2021-05-05 | Building 3 Break Room | Building 3 Kitchen Tap | Faucet | Initial | <5.00 | 2021-06-15
WBG3-01-RM-IN-KIT-CT | 14 | 2021-05-05 | Building 3 Break Room | Building 3 Kitchen Coffee Tap | Coffee Tap | Initial | <5.00 | 2021-06-15
WBG3-01-RM-IN-MECH-IM | 15 | 2021-05-05 | Building 3 Mechanical Room | Building 3 Ice Machine In Mechanical Room | Ice Machine | Initial | <5.00 | 2021-06-15

## Tutoring Center
Date Last Updated |  | 2021-07-08
School Name: |  | Tutoring Center
Lab ELAP ID# |  | NY63556 |  |  | Method of Analysis: |  |  | Metals 200.9
Lab ID# | School Sample ID # | Collection Date | Sample Location | Outlet Description | Initial/ Post Remediation | Lead Result mcg/L (ppb) | Lab Report Reciept Date | Action Taken for Outlets Greater than 15 mcg/L
WTC-01-HA-IN-KIT-T | 1 | 2021-05-13 | Kitchen Tap | Faucet | Initial | <5.00 | 2021-06-15
WTC-01-RM-IN-BT1-T | 2 | 2021-05-13 | Men's Restroom Tap (Near Entrance) | Faucet | Initial | <5.00 | 2021-06-15
WTC-01-RM-IN-GT1-T | 3 | 2021-05-13 | Women's Restroom Tap (Near Entrance) | Faucet | Initial | <5.00 | 2021-06-15
WTC-01-RM-IN-BT2-T | 4 | 2021-05-13 | Men's Restroom Tap (Away From Entrance) | Faucet | Initial | 10.3 | 2021-06-15
WTC-01-RM-IN-GT2-T | 5 | 2021-05-13 | Women's Restroom Tap (Away From Entrance) | Faucet | Initial | 13.1 | 2021-06-15

## Transportation
Date Last Updated |  | 2021-07-08
School Name: |  | Transportation
Lab ELAP ID# |  | NY63556 |  |  | Method of Analysis: |  |  | Metals 200.9
Lab ID# | School Sample ID # | Collection Date | Sample Location | Outlet Description | Initial/ Post Remediation | Lead Result mcg/L (ppb) | Lab Report Reciept Date | Action Taken for Outlets Greater than 15 mcg/L
TRANS-01-RM-IN-BT-T | 1 | 2021-05-13 | Restroom Tap Near Western Entrance | Faucet | Initial | <5.00 | 2021-06-15
TRANS-01-RM-IN-KIT-T | 2 | 2021-05-13 | Kitchen Tap | Faucet | Initial | <5.00 | 2021-06-15
TRANS-01-HA-BY-MO- BF | 3 | 2021-05-13 | Bottle Filler Near Main Office | Bottle Filler | Initial | <5.00 | 2021-06-15
TRANS-01-RM-IN-BT2-T | 4 | 2021-05-13 | Restroom Tap Near Main Office | Faucet | Initial | <5.00 | 2021-06-15
TRANS-01-RM-IN-DRBR-T | 5 | 2021-05-13 | Driver's Break Room Tap | Faucet | Initial | <5.00 | 2021-06-15
TRANS-01-RM-DRBR-CT | 6 | 2021-05-13 | Driver's Break Room Coffee Machine Tap | Coffee Tap | Initial | <5.00 | 2021-06-15
TRANS-01-RM-IN-BT3-T3 | 7 | 2021-05-13 | Men's Restroom Near East Entrance Right Tap | Faucet | Initial | <5.00 | 2021-06-15
TRANS-01-RM-IN-GT-T1 | 8 | 2021-05-13 | Women's Restroom Near East Entrance Left Tap | Faucet | Initial | <5.00 | 2021-06-15
TRANS-01-RM-IN-BT3-T2 | 9 | 2021-05-13 | Men's Restroom Near East Entrance Middle Tap | Faucet | Initial | <5.00 | 2021-06-15
TRANS-01-RM-IN-GT-T2 | 10 | 2021-05-13 | Women's Restroom Near East Entrance Middle Tap | Faucet | Initial | <5.00 | 2021-06-15
TRANS-01-RM-IN-BT3-T1 | 11 | 2021-05-13 | Men's Restroom Near East Entrance Left Tap | Faucet | Initial | <5.00 | 2021-06-15
TRANS-01-RM-IN-GT-T3 | 12 | 2021-05-13 | Women's Restroom Near East Entrance Right Tap | Faucet | Initial | <5.00 | 2021-06-15
TRANS-01-RM-IN-GRG-BF | 13 | 2021-05-13 | Garage Bottle Filler | Bottle Filler | Initial | <5.00 | 2021-06-15